## 1
PART 1 - Preliminary and General Items
ITEM | DESCRIPTION | UNIT | QTY | RATE(KES) | AMOUNT(KES)
1.1 | Contractual Requirements
1.1.1 | Performance Security | LS | 1
1.1.2 | Insurance for loss of or damage to the works, plant, and materials | LS | 1
1.1.3 | Insurance for loss of or damage to Works and Contractor's equipment | LS | 1
1.1.4 | Insurance for loss of or damage to property (except the works, plant, materials, and equipment) in connection with the Contract | LS | 1
1.1.5 | Insurance for personal injury or death | LS | 1
1.1.6 | Establishment and maintenance of Contractor's camp. Including Training Levy | LS | 1
1.2 | GENERAL REQUIREMENTS
1.2.1 | Facilities for the Engineer's Staff
1.2.1.1 | Establishment of Engineer's office at Tiwi Water Office including office furniture and office equipments including water supply and electrical power for he whole project period (18 months) | PS | 1 | 396000 | 396000
1.2.1.2. | Accommodation - 3* Hotel accommodation (incl. Water & Electricity) in single unit bedroom - 1No. Unit for the Resident Engineer and 2 Nr for ARE (1 months) | Day | 30 | 18000 | 540000
1.2.1.3. | Accommodation - Rented and furnished (incl. Water & Electricity) approved accomodation(single unit-3bedrooom)- 1No. Unit for the RE (18 months) | PS | 1 | 1235000 | 1235000
1.2.1.4. | Accommodation - Rented and furnished (incl. Water & Electricity) approved accomodation(single unit-2 bedrooom)- 2 No. Unit for the ARE (36 months) | PS | 1 | 1800000 | 1800000
1.2.2 | Signboards
1.2.2.1 | Signboards, provide | No | 2
1.2.2.2 | Maintain signboards for the duration of the contract | Month | 18
1.2.3 | Equipment for Use by the Engineer's Staff
1.2.3.1 | Surveying equipment to Specifications-Provide and Maintain. Equipment to revert to Employer at end of Contract | PS | 1 | 3000000 | 3000000
1.2.3.2 | Provision of National Standards and International Standards listed in the General Specifications | LS | 1
1.2.4 | Attendance Upon the Engineer's Staff
1.2.4.1 | Drivers provide(2No) | Month | 18
1.2.4.2 | Chainmen provide(3Nos) | Month | 18
1.2.4.3 | Office messenger provide | Month | 18
1.2.4.4 | Watchmen provide(2Nos) | Month | 18
1.2.5 | Testing of Materials
By Third Party Inspection(natural materials)
1.2.5.1 | Cube Test - for an appropriate strength to nr satisfied if the requirements in BS 5328 Part4, clause 3.16 in fulfilled | No | 10
1.2.5.2 | Slump Tests to determine the concrete consistency - in accordance with BS 1881 | No | 10
TOTAL PAGE 1
By Third Party Inspection(man-made other pipes)
1.2.5.3 | Inspection of pipe, fittings, plant manufacturing by the Employer and the Engineer as per Specifications | LS | 1 | 607500 | 607500
1.2.6 | Testing of Works
1.2.6.1 | Water retaining structures constructed in the project including cleansing and sterilization for channels, chambers, at Kaya Bombo, Marere Headworks etc | LS | 1
1.2.7 | Temporary Works
1.2.7.1 | Traffic regulation including charges by KENHA/KERRA | PS | 1 | 350000 | 350000
1.2.7.2 | De-watering | LS | 1
1.2.7.3 | Diversion works at headworks during modification and construction of Flow Division Structure (Provisional) | LS | 1
1.2.7.4 | By-pass pipework where disruption for more than 12 hours is anticipate (Provisional) | LS | 1
1.2.8 | PROVISIONAL SUMS
1.2.8.1 | Labour (carried from Dayworks Schedule) | LS | 1
1.2.8.2 | Materials (carried from Dayworks Schedule) | LS | 1
1.2.8.3 | Plant (carried from Dayworks Schedule) | LS | 1
1.3 | PRIME COST SUMS
1.3.2 | Upkeep and travel for Client's secondment staff | LS | 1 | 450000 | 450000
1.3.3 | Supply and delivery of 4WD double cabin are with dual air bags in the front and AC for the Resident and Assistant Resident Engineers- to revert to Employer - including provision of drivers for the duration of the contract | PS | 2 | 7500000 | 15000000
1.3.4 | Provide for insurance and maintenance and operation of the vehicles for the Engineer's staff during construction period (2 cars) | Month | 18 | 115000 | 2070000
1.3.5 | Provide computer equipment, digital camera, software etc. Reverts to Employer at end of Contract | PS | 1 | 900000 | 900000
1.3.5a | Allow for profits and overheads on Prime Cost and Provisonal Sums(1.2.1.1,1.2.1.2, 1.2.1.3, 1.2.1.4, 1.2.3.1, 1.2.5.3, 1.2.7.1, 1.3.2,1.3.3, 1.3.4, 1.3.5, 1.3.11, 1.3.12 and 1.3.13) | % |  | 27308500
1.3.6 | Compensation and entry upon land | LS | 1
1.3.7 | Investigations of existing and proposed off-take connections along Marere line and Kaya Bombo pipeline location and depth as directed by Engineer. | LS | 1
1.3.8 | Investigations of internal repair works required for reseviors once emptied as director by the Engineer. | LS | 1
1.3.9 | Supply of operation and maintenance tools and equipment for the Boreholes | LS | 1
TOTAL PAGE 2
1.3.10 | HIV/AIDS and COVID-19 prevention sign boards and campaigns | LS | 1
1.3.11 | KWS Wardens assistance in forest areas | PS | 1 | 720000 | 720000
1.3.12 | Provisional sum of Ksh 70,000 for each borehole for acquisition of drilling and abstraction permits from Water Resources Authority, NEMA and County permits. The Contractor will be required to make applications on behalf of CWWDA and ensure timely acquisition of the permits. (2Nos Boreholes) | PC | 2 | 70000 | 140000
1.3.13 | Allow for service inspection by Engineer and Employer for works and installations upon completion | PS | 1 | 100000 | 100000
1.4 | Environmental, Social, Health and Safety (ESHS)
1.4.1 | Resources allocated to ESHS management | LS | 1
1.4.2 | Drafting and updating the ESHS documentation, reporting, inspections | LS | 1
1.4.3 | Implementation of the Health and Safety Plan | LS | 1
1.4.4 | Accommodation, drinking water, meals and transportation of staff
1.4.5 | Training and local recruitment management costs | LS | 1
1.4.6 | Protection of adjacent areas, biodiversity, prevention of erosion and wastewater management | LS | 1
1.4.7 | Traffic, noise and atmospheric emissions management, land take | LS | 1
1.4.8 | Waste and hazardous products management | LS | 1
1.4.9 | Vegetation clearing and Site rehabilitation | LS | 1
TOTAL PAGE 3
TOTAL CARRIED TO GRAND SUMMARY

## 2
PART 2 - Combined hydraulic-chemical well rehabilitation
Required well data
Well name:
Year of construction:
Depth (target value):
Depth (actual value):
Drilling diameter:
Construction diameter:
Casing material:
Well screen material:
Length screen:
Position screen:
Gravel pack:
Pump (type, size, mounting depth):
Rising pipe (diameter, type, individual lengths):
Well house type (shaft, hood or building):
Static Water Level without pumping:
Well performance to date and dynamic water level:
Well performance after rehabilitation and dynamic water level:
Power supply available on site:
Drinking water available on site:
Storage space available on site:
Truck access possible:
ITEM | DESCRIPTION | UNIT | QTY | RATE(KES) | AMOUNT(KES)
Quantities 2.1-2.7 for 1 No of wells
2.1 | Preparatory Measures
2.1.1 | General site facilities to carry out the contractual services in terms of time and quantity, such as storage space, workplaces and parking spaces, machines and equipment of all kinds such as regeneration equipment, drain pipes, settling basins, other pumps and tools, to set up, load, assemble and dismantle water and power supply according to the specifications. | LS | 1
2.1.2 | Construction site clearance after performance of the contract with restoration of the entire area including the access routes used, insofar as the restoration is rendered in individual items of this BoQ. | LS | 1
2.2 | Installation Work
2.2.1 | Removal, cleaning and installation of well and shaft equipment including proper storage. | LS | 1 |  | 0
2.2.2 | Disassembly, cleaning and installation of the rising pipe, U-pump and fittings including disassembly and professional installation of electrotechnical connections. Installation depth up to max. 120 m | LS | 1 |  | 0
2.2.3 | Hose line up to 500 m length Laying to the nearest infiltration or discharge point and dismantle and remove after all work has been carried out. | LS | 1 |  | 0
2.2.4 | Sedimentation tank with a capacity of 10 m³ for drainage of the pumped out regenerate transport, assemble/install and after all work has been carried out disassemble and remove. | LS | 1 |  | 0
0
2.3 | Preliminary and follow-up examinations |  |  |  | 0
2.3.1 | Mobilization and demobilization of the CCTV vehicle including personnel | LS | 1 |  | 0
2.3.2 | Well inspection with color camera (axial and radial perspective) before respectively after regeneration up to 120 m depth | LS | 1 |  | 0
2.3.3 | Protocol of the CCTV inspection before and after the regeneration, triple submission (3 x in writing, 1 x Word file) including photographic recording of anomalies before and after the regeneration (3 x in writing, 1 x jpg file) | No | 2 |  | 0
2.3.4 | Documentation of the CCTV inspection carried out before and after the regeneration incl. submission of two copies of the video log on DVD) | No | 2 |  | 0
2.3.5 | Turbidity-related clear pumping before or during well inspection | LS | 1 |  | 0
2.3.6 | Performance of a pumping test before regeneration with a mobile flow meter to record the current capacity including documentation | LS | 1 |  | 0
0
2.4 | Mechanical and hydraulic pre-cleaning - Desanding |  |  |  | 0
2.4.1 | Mobilization and demobilization of the desanding facility and execution of desanding up to the technical absence of sand (0.1 g/m³) | LS | 1 |  | 0
2.4.2 | Pre-cleaning of the well interior by brushes with variable diameter and the filter slots with adaptable bristle thicknesses including pumping off the dissolved parts according to specifications | LS | 1 |  | 0
2.4.3 | Pre-cleaning of the well interior by means of high pressure including pumping out the dissolved parts. The rotating nozzle head is guided by pump centralizer, the nozzle diameter, the nozzle spacing and the pressure are adjusted to the well lining material and the well diameter. | LS | 1 |  | 0
2.4.4 | Pre-cleaning of the filter gravel by straining with a packer in partial sections of 3.0 m | m | 40 |  | 0
2.4.5 | Suction of the sump pipe up to the base plate | LS | 1 |  | 0
0
TOTAL PAGE 1
2.5 | Hydraulic-chemical intensive cleaning
2.5.1 | Provision, transport and installation of a double surge block (swabbing tool), as per specifictaions (incl. Maintenance and frequent installations as required) | LS | 1 |  | 0
2.5.2 | Performance of a gravel-filling washing (pre-washing) in sections of 3.0 m each / overlapping 0.5 m with a circulating quantity of the regeneration solution adapted to the borehole diameter. The regeneration agent is added during the treatment of the respective section in order to prevent premature drifting in the substrate as described in the specifications. Reaction time 45 minutes. | m | 40 |  | 0
2.5.3 | Straining of the regenerating solution with a packer until it can be proven that no regeneration agent is present. | No | 2 |  | 0
2.5.4 | Performance of a gravel-filling wash (main wash) as described in item 2.5.2. | m | 40 |  | 0
2.5.5 | Straining the regeneration solution with a packer until it can be proven that no regeneration agent is present. | No | 1 |  | 0
2.5.6 | Performing the following measurements during pumping at 15-minute intervals: flow rate, water level, temperature, conductivity | LS | 1 |  | 0
2.5.7 | Treatment and disposal of the pumped regeneration water: Discharge of the first surge of approx. 1 m³ from the respective section into a settling basin. Measurement and documentation of conductivity and sulphate and iron(II) concentration in 15 minute intervals. Subsequent discharge of the clear water phase, in compliance with the FAO limit (3000 μS/cm). Irrigation outside of protection zones I and II or discharge into the sewage system. Disposal of any flocculated oxide sludge together with other sludge from the waterworks in consultation with the client. | LS | 1 |  | 0
0
2.6 | Disinfection and well development |  |  |  | 0
2.6.2 | Performance of a well disinfection according to specifications | LS | 1 |  | 0
2.6.3 | Performance of a pumping test as describe in the specifications. | No | 1 |  | 0
0
2.7 | Documentation |  |  |  | 0
2.7.1 | Preparation and delivery of documentation including daily construction reports, protocols and progress control measurements (3 x written, 1 x Word-/Excel). All measurement results as well as the regeneration process must be documented. - water level measurements - quantities of water - Consumption of regeneration agent per section - Measurements of all required chemical and physical parameters, test rod results and observations - discharge rates - Pump tests including water flow diagrams before/after - Desanding | No | 1 |  | 0
0
| Total for No 1 well: (Pos 2.2 - Pos. 2.7.1) |  |  |  | 0
Provisional Sum Rehabilitation of additional wells as Multiple of "Total for No 1 Well" :
| Rehabilitation of additional wells | PS | 14 |  | 0
TOTAL CARRIED TO GRAND SUMMARY

## 3
PART 3 - PROVISIONAL BILL: Geophysical Investigations
ITEM | DESCRIPTION | UNIT | QTY | RATE(KES) | AMOUNT(KES)
3.1 | Mobilization
3.1.1 | Mobilization/Demobilization of all necessary equipment and staff for proposed tasks to Mombasa/Tiwi | LS | 1
3.2 | Field Work
3.2.1 | Execution of geoelectrical measurements Tiwi: Areas(s) to be covered as presented in the Annex: Tiwi: 1,9 km x 7,4 km (as per dwg 1210/K/015A) Calculations shall include all neccessary field work, cabeling, re-cabeling, Power supplies, as decribed in the specifications | LS | 1
3.2.2 | Report: Presentation of a report with the following, but not limited to results and quality features: The report must also contain a generally understandable summary of the results. Minimum requirements of the report: 1. Title, author, client, customer, date, project number 2. Abstract 3. Geological information: Introduction, location, summary of available knowledge. 4. Up-to-date information: Digital photos of the area at the time of the investigations; description of locations including geology, topography, surface texture, vegetation, soil moisture, weather during data collection, possibly also a rough description of the weather situation before data collection (important for resistance mapping) 5. Method description, reason for the choice of prospecting method and the choice of devices, the measurement point density as well as a detailed device description 6. Deep position of the aquifer, salinities, additional information on layers and sublayer as well as on capacity. 7. Results, description and interpretation-see also points IV and V. vii) Summary 8. Data presentation as color pictures, topography and interpretation plan Three copies of the report as well as three copies of the electronically stored raw data and the processed data must be made available to the client | LS | 1
TOTAL CARRIED TO GRAND SUMMARY - Provisional Sum

## 4
PART 4 - Drilling, Construction, Test Pumping of 2 No. New Wells (1 No. at Site A and 1 No. at Site 9)
Item | Description | Unit | Qty | Rate(KES) | Amount(KES) | Qty | Amount in EURO | BH 11 | BH 06 | BH 02 | BH 10 | BH 13 | BH 14 | TOTAL Qty | Amount in EURO | Qty | Amount in EURO
4.1 | Mobilisation, Setting up & Demobilisation
4.1.1 | Mobilisation and demobilisation of drilling rig and test pumping unit | LS | 1 |  |  | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0 | 1 | 0
4.1.2 | Transportation of drilling rig and test pump unit to site | LS | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
4.1.3 | Transportation of drilling rig and test pump unit to second site | LS | 1
4.2 | DRILLING OF BOREHOLES
4.2.1 | Rotary drilling techniques should be used for drilling of boreholes, 17" final diameter, depth up to 120 m according to specifications including sampling as per technical specifications | m | 240 |  |  | 855 | 0 | 92 | 78 | 82 | 91 | 82 | 88 | 513 | 0 | 1368 | 0
4.3 | Well Construction
4.3.1 | Supply and Installation of a sanitary seal (MS) to 5 m, the borehole shall be grouted using cement slurry of 1.85 - 2.15 kg cement/liter including the steel standpipe for stabilisation purposes, according to specifications | m | 10
4.3.2 | Supply and Installation of plain casing (PVC with a minimum wall thickness of 6 mm and a diamter of 200 mm), according to specifications | m | 140 |  |  | 263.59 | 0 | 59.45 | 0 | 54.83 | 66.52 | 57.83 | 57.59 | 296.22 | 0 | 559.81 | 0
4.3.3 | Supply and Installation of screen casing (uPVC with a minimum wall thickness of 6 mm and a diameter of 200 mm), according to specifications | m | 100 |  |  | 96.33 | 0 | 18.27 | 0 | 18.25 | 21.34 | 15.25 | 30.37 | 103.48 | 0 | 199.81 | 0
4.3.4 | Installation of a 3/4" Observation Pipe in the borehole, for Water level Measures, max. length: 100 m; Material; PVC wiith a locked cap. | m | 200
4.3.5 | Supply and installation of bottom plug (wooden or PVC) | No | 2 |  |  | 4 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 5 | 0 | 9 | 0
4.3.6 | Supply and installation of gravel pack (consist of washed, well-rounded particles of a uniform grading of between 0.3 to 4.0 mm, shall comprise 90% siliceous material and must contain no clay, shale, silt, fines, excessive amounts of calcareous material or crushed rock - Kilindini- Sands), according to specifications | m³ | 10 |  |  | 12.1 | 0 | 1.8 | 0 | 1.9 | 2 | 1.8 | 1.8 | 9.3 | 0 | 21.4 | 0
4.3.7 | Clay sealing, back fill and grouting | No | 2 |  |  | 4 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 5 | 0 | 9 | 0
4.3.8 | Well development, according to specifications | hr | 48 |  |  | 22.5 | 0 | 9 | 0 | 5 | 5 | 5 | 5 | 29 | 0 | 51.5 | 0
4.3.9 | Well disinfection, according to specifications | No | 2 |  |  | 4 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 5 | 0 | 9 | 0
TOTAL PAGE 1
4.4 | Test Pumping
4.4.1 | Step testing, 3 duty points, 144 hours, incl. all for the correct performance of the task necessary installations, pumps, pipes, erosion protection | hr | 288 |  |  | 258.5 | 0 | 72 | 0 | 0 | 72 | 72 | 72 | 288 | 0 | 546.5 | 0
4.4.2 | Recovery test | hr | 48 |  |  | 19 | 0 | 4 | 0 | 0 | 4 | 7 | 6 | 21 | 0 | 40 | 0
4.5 | Well Completion
Supply and install submersible pump, according to the results of the test pumping - refer to BoQ Part 5
4.5.1 | Prepare and submit testing pumping Report as per specifications. | LS | 2 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 0
4.5.2 | Construct apron / concrete slab and concrete housing of well incl. well head with all necessary installations, openings in the suitable size and material for the required functionality of the well | No | 2 |  |  | 4 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 5 | 0 | 9 | 0
4.6 | Miscellaneous Works
4.6.1 | Water quality sampling - testing the physic-chemical and bacteriological quality . (minimum of 4 suitable two-liter capacity water containers) | LS | 2 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 0
4.7 | PROVISIONAL SUMS
4.7.1 | Provisional sums for additional max 5 new boreholes, as per above positions | PS | 5 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4.7.2 | Stand by time (provisional sum) for 8 hours per day max | Days | 28
| TOTAL PAGE 2 | [5 empty] | 0 | [7 empty] | 0 |  | 0
TOTAL CARRIED TO GRAND SUMMARY

## 5.1_BHA
PART 5.1 - Electro-Mechanical Works & Pipeworks Borehole A (Site-Replacement)
ITEM | DESCRIPTION | UNIT | QTY | Rate(KES) | Amount(KES)
5.1.1 | Electro-Mechanical Works:
Items below are given for assumed pump capacity, final specifications (e.g. cable thickness) and quantity are dependent on type of pump and pumping depths and have to be identified by the contractor after test pumping
SUPPLY, DELIVER TO SITE, INSTALL AND TEST:
5.1.1.01 | Submersible pump set of capacity 40 m3/hr. of water against a total head of 135 metres directly coupled to 3 phase, 415 vac motor, with pump suction inlet at 54 metres below ground level. | Nr | 1
5.1.1.02 | Overheads and profits on item 5.1.1.01 as specified for Prime Cost sum items | %
5.1.1.03 | 16 mm2/4 core submersible pump flat cable | m | 58
5.1.1.04 | DN6x120 mmL stainless steel water level control electrodes. | Pair | 1
5.1.1.05 | OD25 class D uPVC dipper pipe | m | 55
5.1.1.06 | DN100 GS class C threaded water pipe. | m | 55
5.1.1.07 | DN100 GS steam sockets | Nr | 12
5.1.1.08 | DN100x300 mm long GI starter pipe | Nr | 1
5.1.1.09 | 0.75mm2 sc double insulated copper cable( brown and black) each 53 metres | m | 106
5.1.1.10 | Lay in trench/duct, connect and test 1.5 mm2/2c pvc swa pvc copper cable | m | 35
5.1.1.11 | Lay in trench/duct, connect and test 16 mm2/4c armoured copper cable | LM | 35
5.1.1.12 | Copper cable gland c/w lock-nut and shroud for 16 mm2/4 core pvc swa pvc copper cable. | Nr | 2
5.1.1.13 | Copper cable gland c/w lock-nut and shroud for 1.5 mm2/2 core pvc swa pvc copper cable | Nr | 2
5.1.1.14 | 18.5 Kw, 3 phase, 415 vac, soft starter panel including integral 3 phase surge arrestor unit. | SET | 1
5.1.1.15 | Masory earth rod chamber of internal size 250x250 x300 mmH extending 50 mm above the ground. It shall be constructed from 150x150x450 mmL masonry blocks (1:3:6). It shall be c/w 75 mm thick perforated cover (1:2:4). | Nr | 1
5.1.1.16 | D15x2.4 metre copper earth rod c/w clamp in a masonry chamber. | Nr | 1
5.1.1.17 | 25 mm2 sc copper cable (green) | m | 5
TOTAL PAGE 1
5.1.1.18 | Supply and install water-tight GS cable junction box of size 125x125x90mm depth, fabricated from 3 mm thick plate.. It shall have GS DIN plate fixed at the inside centre but raised by 10 mm from back side, 3 No. 10 amps and 5 No. 60 amps cable terminal blocks mounted on the plate, tough rubber cable grommets for 16mm2/4c and 0.75 mm2 sc submerssible cables. | Nr. | 1
5.1.1.19 | DN38x150 mmL GS threaded pipe piece (cable entry) | Nr. | 1
5.1.1.20 | Supply and installation of Well Probe Sensor complete with well probe cable of size 0.75 mm² of 70 m (to be determined after test pumping). | SET | 1
5.1.1.21 | Supply, installation, testing and commissioning of Electro Magnetic Flow Meter, DN 80, Qmax=80m3/hr, Qnom=40m3/hr, QT=8m3/hr and Qmin=1.2m3/hr, 2 battery power supply, IP 68, RS232 and RS 485 outputs. | Nr. | 1
5.1.1.22 | Supply, installation, testing and commissioning of Hydrostatic Level Transmitter with integrated Pt 100 temperature sensor 0-700C, range from 1-100 mH2Og, acuracy + 0.175% FS BSL NLHR>4mH2O, +o.25%<4mH2O. | Nr. | 1
5.1.1.23 | INSTALLATION SUNDRIES
5.1.1.23a | ID220x4 mm Thick GS Borehole cap with welded DN100 GS pipe piece, welded DN44 GI slow bend for passage of 16mm2/4c cable, water level control electrodes cables and passage of OD25 mm pvc dipper pipe. | Nr. | 1
5.1.1.23b | Boss white (200 gm tin) | pc | 3
5.1.1.23c | 550 mm plastic cable tie | Nr. | 40
5.1.1.23d | 20 mm Wx9ML self bonding electrical tape (scotch 23) | ROLL | 2
5.1.1.23e | 12 mm Wx12 ML PTFE thread seal tape | ROLL | 15
5.1.1.23f | 20 mm high quality electrical pvc tape (Red, Yellow, Blue, Black) | ROLL | 4
5.1.1.23g | Stainless steel ferrules for 16 mm2 cable | Nr. | 4
New Mains Power Control Swichgear Panel and Switch gear/Office Building Wiring
5.1.2 | Mains Power Control Switchgear Panel
5.1.2.01 | Free standing, 250 amps, 3 phase, 415 vac, compact, compartmented, indoor, surface metal clad maiins power control panel (IP20), dust-proof, termite-proof, comprising of but not limited to the following, duly wired and labeled. It shall be constructed from gauge 16 spangled sheet steel of minimum thickness 1.75mm; | Nr. | 1
5.1.2.02 | Kenya Power & Lighting Company CUT-OUTS chamber | Nr. | 1
5.1.2.03 | 1xKPLC incommer Current transformers chamber | Nr. | 1
5.1.2.04 | 1xKPLC metering equipment chamber incommer Current transformers chamber | Nr. | 1
5.1.2.05 | 1x250 amps adjustable triple pole mccb (adjustable range: 0.7IN, 0.8IN, 0.9IN, 1.0IN set at 0.8IN where IN= rated current of mccb = 250 amps). | Nr. | 1
5.1.2.06 | 1x20 Kvar, 3 phase, 415 vac, 5 step central automatic power capacitor correction bank c/w 100 amps TP supply mccb, contactors, fuses, programmable electronic PF controller.relay etc. | Nr. | 1
5.1.2.07 | 1xsingle phase, 240 vac kWh energy registering meter | Nr. | 1
5.1.2.08 | 4x260 amps high conductivity rectangular bare copper bus-bar conductors. | Nr. | 1
5.1.2.09 | 2x100 amps, TP, 415 vac, mccbs, ICU =15 kA. Each in its own compartment (for Boreholes). | Nr. | 1
5.1.2.10 | 1x63 amps, TP, 415 vac, mccbs, ICU =15 kA. Each in its own cmpartment. (Spares) | Nr. | 1
5.1.2.11 | 1x3 phase, 415 vac surge divertor c/w protective mcbs on main 250 amps mccb terminals. | Nr. | 1
TOTAL PAGE 2
5.1.2.12 | 1x125 amps,1phase, 240 vac class "A" mcbs (Building Distribution Board) | Nr | 1
5.1.2.13 | 1x Cooling fan rated 25 watts, 240 vac, 2800 rpm continuously rated installed on the side, 100 mm height from the bottom clw filter and termite-proof, dust-proof stainless steel protection D1.5 mm wiregauze. | Nr | 1
5.1.2.14 | 2x ventillation hole of size 150x100 mm installed on the top opposite sides, 50 mm below top c/w termite-proof, dust-proof filter and grid. | Nr | 1
5.1.2.15 | 1x3 phase, 240 vac network analyzer/recorder (voltage/current/kWh/Pf/Hz) resettable, as MCAplus, Circutor Smart or similar quality approved make with LED phase indicators (RED, YELLOW, BLUE) on front panel. | Nr | 1
5.1.2.16 | 100 amps, 6 way, 1 phase, 240 vac DIN distribution board; c/w; 2 No. 10 amps, 1 pole, 240 vac class "A" mcbs, 3 No. 20 amps, 1 pole class "A" mcbs, 1 No. Blanking plate. | Nr | 1
5.1.2.17 | 3xAC ammeters range 0-300 amps c/w CTS. | Nr | 1
5.1.7.18 | 1xAC voltmeter (0-500 vac) c/w vss and protection mcbs. | Nr | 1
5.1.2.19 | 250 amps, 415 vac TPN manual changer-over switch c/w pilot indicator lights ( KPLC ON, KPLC LOAD ON, GENERATOR ON, GENERATOR LOAD ON etc). | Nr | 1
5.1.2.20 | 32 amps, TPN + E (5-pin), 415 vac, socket outet (smc) c/w isolator, base and screw top lid.
5.1.2.21 | 25x3 mm thick copper strip bound along the switchgear panel length (earthing) | SET | 1
5.1.3 | Electrical Repairs of Mains Power Control Switchgear/Office Building
5.1.3.01 | Remove the existing socket/lighting wiring. | LS | 1
5.1.3.02 | 20 mm diam. GS conduit fixed on the walls and roof members. The cost shall be inclusive of tees, bends, circular boxes with covers, other necessary accessories | m | 40
5.1.3.03 | 1.5 mm2 single copper cables (Red=80 m, Black=50 m , Green =50 m) laid in GS conduit and terminated at boh ends. | m | 180
5.1.3.04 | 2.5 mm2 single copper cables (Red=25 m, Black=25 m , Green =25 m) laid in GS conduit and terminated at boh ends. | m | 90
5.1.3.05 | 10 amps, 1 way 2 gang switch (smc) as Mem, Crabtree or similar quality approved make c/w box and ss screws | Nr | 1
5.1.3.06 | 10 amps, 1 way 1 gang switch (smc) as Mem, Crabtree or similar quality approved make c/w box and ss screws | Nr | 1
5.1.3.07 | 13 amps, 240 vac, single switched socket outlet (smc) as Mem, Crabtree or similar quality approved make c/w box stainless steel screws (ringmain circuit). | Nr | 4
5.1.3.08 | 36 wattsx1200 mmL single fluorescent lighting fitting, energy save, water tight (IP 20), metal body, corrossion resistant, power factor compensated, c/w tube, starter mounted on ceiling but 20 mm off the surface using 20 mm diam. GS coupler) | Nr | 2
5.1.3.09 | 20 wattsx300 mmL LED fluorescent lighting fitting (IP54), energy save, corrossion resistant, power factor compensated. | Nr | 4
TOTAL PAGE 3
5.1.3.10 | 2.5 mm2 single core copper cables (Red= 10 m, Black=10 m, Green= 10 m )wired in 20 mm diameter pvc conduit from consumer unit to fan speed control unit and fan terminals. | m | 30
5.1.3.11 | 3 blade, adjustable slow speed (0-300 rpm), 240 vac ceiling mounted cooling fan c/w speed adjustable control unit completely wired (in conduit). | SET | 1
5.1.3.12 | AC/DC POWER SUPPLY
5.1.3.12.01 | Floor stand supported, 240 ac, 2.5 amps/24 vdc, 20 amps continuosly rated converter fully protected (overload/short-circuit/reverse voltage and polarity etc c/w RJ45, RS232, RS485 ports, mcbs protected outputs to supply water meter, borehole water level measurement, rising main pressure measurement, PLC, Radio/Data Trans-Receiver Equipment. | SET | 1
5.1.4 | Fire Fighting Equipment
5.1.4.01 | 5 Kg Class ABC Powder steel cylinder fire extinguisher, c/w pressure gauge wall mounting steel bracket , operating instructions and accessories, fully charged. | Nr | 2
5.1.5 | Other Electro-Mechanical Works
5.1.5.01 | Improve lightning protection system | LS | 2
5.1.5.02 | Disconnection and handing over to the Employer the entire existing electrical installations | LS | 1
5.1.5.03 | Preparation of all design technical and working drawings for the works for approval prior to commencement of installation of works as per the Specifications. | LS | 1
5.1.5.04 | Allow for all the builders works associated with all the electrical works that the contractor considers necessary to complete works | LS | 1
5.1.5.05 | Painting, varnishing and any other works necessary for making good all the disturbed areas as a result of the new electrical installations. | LS | 1
5.1.5.06 | Supply, installation, testing and commissioning of Amplified Pressure Transmitter with pressure range of 20 bar, over pressure safety of 50 bar, from SS material, and power supply 10<UCB<30 VDC and signal output 4-20 mA 2-wire system. | Nr | 1
5.1.5.09 | ID8x3 mm Thick GS tube c/w all necessary mounting fittings, bends etc enclosed in DN15 GI pipe for connection on GS rising main and laid in trenching/duct and connection on pressure switch, pressure gauge at the power supply control room. | m | 35
5.1.5.10 | Adjustable Pressure switch in IP54 metal enclosure, with dual scale (Kg/cm2 and Bar), range 0 - 20 Kg/cm2 (0-20 Bar) connected to GS copper tube and fixed firmly on the wall by GS bracket.. It shall have integral 2NO+2NC auxillary contacts rated 10 amps, 240 vac, stainless steel isolation ball valve. | Nr | 1
5.1.5.11 | High quality pressure gauge - IP54, with dual scale (Kg/cm2 and Bar).Range (0 - 20 Kg/cm2 )/(0 - 20 bar). It shall be c/w all fitting accessories for connecting on ID8x3mm GS tube. It shall be c/w stainless steel isolation ball valve. | Nr | 1
5.1.5.12 | Single orifice cast steel air valve c/w accessories for mounting on DN100 GS pipe | Nr | 1
5.1.5.13 | Supply, installation, testing and commissioning of 24V DC Power Supply Unit, 500VAC Equipped with one input fuse,187 – 264 VAC, 47 to 63 Hz,0°C….+45°C,≥ IP20, | Nr | 1
5.1.5.14 | Supply, installation and testing of Input /Output interface module (I/O), min. 4 analog inputs 0-10V, 0-20mA, 4-20mA programmable, min 2 digital inputs with frequency range 0-16 Hz | Nr | 1
5.1.5.15 | Supply, installation and testing of Class 10 GPRS Modem, Dual-Band E-GSM/GPRS 900/1800 MHz,GPRS multi-slot class 10,1W@900 MHz,1W@ 1800 MHz,Control via AT commands, -200 C to +550C,RS 232 interface,TCP/IP protocol stack for M2M | Nr | 1
5.1.5.16 | Supply and installation of 1.5mm² armoured underground cable for the well probe. | m | 35
TOTAL PAGE 4
5.1.6 | Pressure Pipes and Fittings:
Modification of the connection between the new pump, the suction and the discharge pipes and fittings, and for corresponding concrete works.
5.1.6.01 | Disconnection, dismantling and disposal of old pipes, pipe fittings, valves, water meter. | LS | 1
Supply, delivery to Site, Install and Test:
5.1.6.02 | DN 100 mm, PN 16 bar non-slam, non-return valve. | Nr | 1
5.1.6.03a | DN 100 mm, PN 16 bar gate valve c/w hand wheel. | Nr | 1
5.1.6.03b | DN 100xPN 16 bar gate valve (threaded c/w hand wheel. | Nr | 1
5.1.6.04 | DN 100 mm, PN 16 bar Y-strainer | Nr | 1
5.1.6.05 | DN100x200 mmL GS pipe piece (threaded) with bore for mounting an air valve. | Nr | 1
5.1.6.06 | DN100x1500 mmL GS pipe piece (threaded). | Nr | 1
5.1.6.07 | DN100x250 mmL GS pipe piece, flanged on one side and plain at the opposite end. | Nr | 6
5.1.6.08 | DN100x90o GS slow bend (threaded) | Nr | 4
5.1.6.09 | DN100 GS socket (threaded) | Nr | 4
5.1.6.10 | DN100 double flanged GS equal Tee | Nr | 1
5.1.6.11 | DN100 steel Johnson coupling c/w rubber rings. | Nr | 4
5.1.6.12 | 100mmWx5 mm thick rubber gasket | m | 2
5.1.6.13 | DN100x1200 mmL GS pipe piece threaded. | Nr | 2
5.1.6.14 | DN100x2500 mmL GS pipe piece (threaded). | Nr | 2
5.1.6.15 | DN100 steel union | Nr | 3
5.1.6.16 | DN100 GS male bush | Nr | 4
5.1.6.17 | Any other accessories required for the system | LS | 1
5.1.7 | Removal Of Old Items And Trenching
5.1.7.01 | Excavate, expose and remove existing cables ( power control room to borehole). Trim the trenching to size 450 mmWx500 mm depth. Back fill to ground level after laying of cable. Cart away, dispose excess as advised. | m | 30
5.1.7.02 | Break existing RC pipe support block. | Nr | 2
5.1.7.03 | Excavate to expose and remove a section of existing DN 100 GS Borehole-Rising main inter-connection pipe work. Trim the trenching to size 500 mmW900 mm depth. Back fill to ground level after laying of cable. Cart away , dispose excess as advised. | m | 5
TOTAL PAGE 5
TOTAL BH A:- CARRIED TO BILLL 5 SUMMARY SHEET

## 5.2_BHC
PART 5.2 - Electro-Mechanical Works & Pipeworks Borehole C (Site-Repairs)
ITEM | DESCRIPTION | UNIT | QTY | Rate(KES) | Amount (KES)
ITEM | ITEM DESCRIPTION | UNIT | QTY | Rate(KES) | Amount(KES)
5.2.1 | Electro-Mechanical Works
Items below are given for assumed pump capacity, final specifications (e.g. cable thickness) and quantity are dependent on type of pump and pumping depths and have to be identified by the contractor after test pumping
SUPPLY, DELIVER TO SITE, INSTALL AND TEST:
5.2.1.01 | Submersible pump set of capacity 44m3/hr. of water against a total head of 156 metres directly coupled to 3 phase, 415 vac motor, with pump suction inlet at 55 metres below ground level. | nr | 1
5.2.1.02 | Overheads and profits on item 5.2.1.01 as specified for Prime Cost sum items | %
5.2.1.03 | 16 mm2/4 core submersible pump flat cable | m | 58
5.2.1.05 | DN6x120 mmL stainless steel water level control electrodes. | Pair | 1
5.21.06 | OD25 class D uPVC dipper pipe | m | 54
5.2.1.07 | DN100 GS class C threaded water pipe. | m | 55
5.2.1.08 | DN100 Steel steam sockets | Nr | 12
5.2.1.09 | DN100x300 mm long GS starter pipe (threaded) | Nr | 1
5.2.1.10 | 0.75mm2 sc double insulated copper cable( brown and black) each 76 metres | m | 116
5.2.1.11 | Lay in trench/duct, connect and test 1.5 mm2/2c pvc swa pvc copper cable (starter panel to borehole) | m | 15
5.2.1.12 | Lay in trench/duct, connect and test 10 mm2/4c armoured copper cable | m | 15
5.2.1.13 | Copper cable gland c/w lock-nut and shroud for 16 mm2/4 core pvc swa pvc copper cable. | Nr | 2
5.2.1.14 | Copper cable gland c/w lock-nut and shroud for 1.5 mm2/2 core pvc swa pvc copper cable. | Nr | 2
5.2.1.15 | Supply and install water-tight GS cable junction box of size 150x150x90mm depth, fabricated from 3 mm thick plate.. It shall have GS DIN plate fixed at the inside centre but raised by 10 mm from back side. 3 No. 10 amps and 5 No. 80 amps cable terminal blocks mounted on the plate, tough rubber cable grommets for 16mm2/4c and 0.75 mm2 sc submerssible cable. | Nr | 1
5.2.1.16 | 30 Kw, 3 phase, 415 vac, soft starter panel including integral 3 phase surge arrestor unit. The cost shall be inclusive 10 mm2/4c armoured copper cable, cable glands etc for connection from starter panel to main switchgear. | SET | 1
5.2.1.17 | DN38x150 mmL GS threaded pipe piece (cable entry) | Nr | 1
5.2.1.18 | Supply and installation of Well Probe Sensor complete with well probe cable of size 0.75 mm² of 75 m (to be determined after test pumping). | SET | 1
5.2.1.19 | Supply, installation, testing and commissioning of Electro Magnetic Flow Meter, DN80, Qmax=80m3/hr, Qnom=40m3/hr, QT=8m3/hr and Qmin=1.2m3/hr, 2 battery power supply, IP 68, RS232 and RS 485 outputs. | Nr | 1
TOTAL PAGE 1
5.2.1.20 | Supply, installation, testing and commissioning of Hydrostatic Level Transmitter with integrated Pt 100 temperature sensor 0-700C, range from 1-100 mH2Og, acuracy + 0.175% FS BSL NLHR>4mH2O, +o.25%<4mH2O. | No | 1
5.2.1.21 | Installation Sundries
5.2.1.21a | ID220x4 mm Thick GS Borehole cap with welded DN100 GS pipe piece, welded DN38 GS slow bend for passage of 16mm2/4c cable, water level control electrodes cables and passage of OD25 mm pvc dipper pipe. | Nr | 1
5.2.1.21b | Boss white (200 gm tin) | pc | 2
5.2.1.21c | 450 mm plastic cable tie | Nr | 25
5.2.1.21d | 20 mm Wx9ML self bonding electrical tape (scotch 23) | ROLL | 2
5.2.1.21e | 12 mm Wx12 ML PTFE thread seal tape | ROLL | 10
5.2.1.21f | 20 mm high quality electrical pvc tape (Red, Yellow, Blue, Black) | ROLL | 4
5.2.1.21g | Stainless steel ferrules for 16mm2 cable | Nr | 4
5.2.1.21h | Stainless steel ferrules for 0.75 mm2 cable | Nr | 3
5.2.1.22 | Other Electro-mechanical Works - BH C
5.2.1.22a | Preparation of all design technical and working drawings for the works for approval prior to commencement of installation of works as per the Specifications. | LS | 1
5.2.1.23b | Allow for all the builders works associated with all the electrical works that the contractor considers necessary to complete works | LS | 1
5.2.1.22c | Painting, varnishing and any other works necessary for making good all the disturbed areas as a result of the new electrical installations. | LS | 1
5.2.1.22d | Supply, installation, testing and commissioning of Amplified Pressure Transmitter with pressure range of 20 bar, over pressure safety of 50 bar, from SS material, and power supply 10<UCB<30 VDC and signal output 4-20 mA 2-wire system. | Nr | 1
5.2.1.22e | ID8x3 mm Thick GS tube c/w all necessary mounting fittings, bends etc enclosed in DN15 GS pipe for connection on GS rising main and laid in trenching/duct and connection on pressure switch, pressure gauge at the power supply control room. | m | 10
5.2.1.22f | Adjustable Pressure switch in IP54 metal enclosure, with dual scale (Kg/cm2 and Bar), range 0 - 25 Kg/cm2 (0 - 25 Bar) connected to GS copper tube and fixed firmly on the wall by GS bracket. It shall have integral 2NO+2NC auxillary contacts rated 10 amps, 240 vac, stainless steel isolation ball valve. | Nr | 1
5.2.1.22g | High quality pressure gauge - (indoor mounting), with dual scale (Kg/cm2 and Bar).Range (0 - 30 Kg/cm2 )/(0 - 30 bar). It shall be c/w all fitting accessories for connecting on ID8x3mm GS tube. It shall be c/w stainless steel isolation ball valve. | Nr | 1
5.2.1.22h | Single orifice cast steel air valve c/w accessories for mounting on DN100 GS pipe. | Nr | 1
5.2.1.22i | Supply, installation, testing and commissioning of 24V DC Power Supply Unit, 500VAC Equipped with one input fuse, 187 – 264 VAC, 47 to 63 Hz,0°C….+45°C,≥ IP20. | Nr | 1
5.2.1.22j | Supply, installation and testing of Input /Output interface module (I/O), min. 4 analog inputs 0-10V, 0-20mA, 4-20mA programmable, min 2 digital inputs with frequency range 0-16 Hz. | Nr | 1
TOTAL PAGE 2
5.2.1.22k | Supply, installation and testing of Class 10 GPRS Modem, Dual-Band E-GSM/GPRS 900/1800 MHz,GPRS multi-slot class 10,1W@900 MHz,1W@ 1800 MHz,Control via AT commands, -200 C to +550C,RS 232 interface,TCP/IP protocol stack for M2M | Nr | 1
5.2.1.22l | Supply and installation of 1.5mm² armoured underground cable for the well probe. | m | 15
5.2.1.23 | Pressure Pipes and Fittings:
Modification of the connection between the new pump, the suction and the discharge pipes and fittings, and for corresponding concrete works.
5.2.1.23a | Disconnection, dismantling and disposal of old pipes, pipe fittings, valves, water meter. | LS | 1
Supply, delivery to Site, Install and Test:
5.2.1.23b | DN100x90o GI slow bend with a bore for pressure gauge | Nr | 1
5.2.1.23c | DN100 GI socket with bore for mounting air valve | Nr | 1
5.2.1.23d | DN100x1200 GI pipe piece (threaded at both ends) | Nr | 2
5.2.1.23e | DN100x300 GI pipe piece (threaded at both ends) | Nr | 1
5.2.1.23f | DN100x90o GI slow bend | Nr | 2
5.2.1.23g | DN100 GI hex nipple | Nr | 4
5.2.1.23h | DN100 GS union | Nr | 3
5.2.1.23i | DN100xPN16 steel Non-slam Non-Return valve. | Nr | 1
5.2.1.23j | DN100xPN16 steel gate valve c/w handwheel | Nr | 2
5.2.1.23k | DN100x250 mmL GS pipe piece | Nr | 2
5.2.1.23l | DN100x2500 mmL GS pipe piece. | Nr | 1
5.2.1.23m | DN100 steel Johnson coupling c/w rubber rings. | Nr | 3
5.2.2 | Removal Of Old Items And Trenching
5.2.2.01 | Excavate, expose and remove existing cables ( power control room to borehole). Trim the trenching to size 450 mmWx500 mm depth. Back fill to ground level after laying of cable. Cart away, dispose excess as advised. | m | 15
5..2.2.02 | Excavate, expose and remove a section of existing DN100 GI Borehole-rising main inter-connection pipe work. Trim the trenching to size 500 mmWx600 mm depth. Back fill to ground level after laying of pipe. Cart away, dispose excess as advised. | m | 3
TOTAL PAGE 3
5.2.3 | REHABILITATION OF MAINS POWER CONTROL SWITCHGEAR PANEL, ELECTRICAL WIRING OF SWITCHGEAR/OFFICE/SANITATION BUILDING AND FIRE FIGHTING EQUIPMENT
5.2.3.1 | MAINS POWER CONTROL SWITCHGEAR PANEL
5.2.3.1.01 | Open the mains power switchgear panel, carefully clean, dust and air blows the compartments. Tighten any loose, cables, bolts and nuts | Item | 1
5.2.3.1.02 | Install 3 phase, 415 vac surge divertor c/w protective mcbs. | Nr | 1
5.2.3.1.03 | Install 15 Kvar, 3 phase, 415 vac, 4 step automatic power capacitor correction bank. | Set | 1
5.2.3.1.04 | Remove the defective cooling fan. Install a new one rated 25 watts, 240 vac at 100 mm height from the bottom of the panel c/w dust-prooof filter and protective GS wire frame (2x2xD1.5 mm). Install where the defective fan has been removed from, protective GS grid (2x2xD1.5 mm) c/w filter . | Set | 1
5.2.3.2 | MAINS POWER CONTROL SWITCHGEAR/OFFICE/WC BUILDING WIRING
5.2.3.2.01 | Remove the existing socket/lighting wiring, replace the defective sections of conduit | Item | 1
5.2.3.2.02 | Re-wire the lighting circuits using 1.5 mm2 single copper cables (Red=90 m, Black=70 m , Green =70 m). | m | 230
5.2.3.2.03 | Re-wire the sockets circuits using 2.5 mm2 single copper cables (Red= 60 m, Black=60 m , Green = 60 m) | m | 180
5.2.3.2.04 | 10 amps, I way 2 gang switch (IVY white, flush) as Mem, Crabtree or similar quality approved make. | Nr | 1
5.2.3.2.05 | 13 amps, 240 vac, twin switched socket outlet (IVY White, flush) as Mem, Crabtree or similar quality approved make c/w stainless steel screws (ringmain circuit). | Nr | 3
5.2.3.2.06 | 36 wattsx1200 mmL single fluorescent lighting fitting, energy save, water tight (IP 20), metal body, corrossion resistant, power factor compensated, c/w tube, starter mounted on ceiling but 20 mm off the surface using 20 mm diam. GS coupler) | Nr | 2
5.2.3.2.07 | 20 wattsx300 mmL LED fluorescent lighting fitting (IP54), energy save, corrossion resistant, power factor compensated. | Nr | 4
5.2.3.2.08 | Masory earth rod chamber of internal size 250x250 x300 mmH extending 50 mm above the ground. It shall be constructed from 150x150x450 mmL masonry blocks (1:3:6). It shall be c/w 75 mm thick perforated cover (1:2:4). | Nr | 1
5.2.3.2.09 | D15x2.4 metre copper earth rod c/w clamp in a masonry chamber.. | Nr | 1
5.2.3.2.10 | 25 mm2 sc copper cable laid trench and connected to earth rod and main switchgear panel earth bond tape. | m | 3
5.2.3.2.11 | 3 blade, adjustable slow speed (0-300 rpm), 240 vac ceiling mounted cooling fan c/w speed adjustable control unit completely wired (in conduit). | SET | 1
5.2.3.2.12 | 32 amps, TPN + E (5-pin), 415 vac, socket outet (smc) c/w isolator, base and screw top lid, wired using 6 mm2 sc copper cables in 32 mm diameter GS conduit. | No | 1
5.2.4 | Fire Fighting Equipment
5.2.4.01 | 5 Kg Class ABC Powder steel cylinder fire extinguisher, c/w pressure gauge wall mounting steel bracket , operating instructions and accessories, fully charged. | Nr | 2
5.2.5 | AC/DC POWER SUPPLY
5.2.5.01 | Floor stand supported, 240 ac, 2.5 amps/24 vdc, 20 amps continuosly rated converter fully protected (overload/short-circuit/reverse voltage and polarity etc c/w RJ45, RS232, RS485 ports, mcbs protected outputs to supply water meter, borehole water level measurement, rising main pressure measurement, PLC, Radio/Data Trans-Receiver Equipment. | SET | 1
TOTAL PAGE 4
TOTAL BH C:- CARRIED TO BILLL 5 SUMMARY SHEET

## 5.3_BH D2,D3
PART 5.3 - Electro-Mechanical Works & Pipeworks Borehole D2, D3 (Site Repairs)
5.3.1 BOREHOLE D2
ITEM | ITEM DESCRIPTION | UNIT | QTY | Rate(KES) | Amount(KES)
5.3.1.1 | Electro-Mechanical Works
Items below are given for assumed pump capacity, final specifications (e.g. cable thickness) and quantity are dependent on type of pump and pumping depths and have to be identified by the contractor after test pumping
5.3.1.1.01 | Submersible pump set of capacity 40m3/hr. of water against a total head of 165 metres directly coupled to 3 phase, 415 vac motor, with pump suction inlet at 42 metres below ground level. | nr | 1
5.3.1.1.02 | Overheads and profits on item 5.3.1.1.01 as specified for Prime Cost sum items | %
5.3.1.1.03 | 10 mm2/4 core submersible pump flat cable | m | 44
5.3.1.1.04 | DN6x120 mmL stainless steel water level cotrol electrodes. | pairs | 1
5.3.1.1.05 | OD25 class D uPVC dipper pipe | mm | 42
5.3.1.1.06 | DN75 GS class C threaded water pipe. | m | 42
5.3.1.1.07 | DN75 GS steam sockets | Nr | 12
5.3.1.1.08 | DN75x300 mm long GS starter pipe | Nr | 1
5.3.1.1.09 | 0.75mm2 sc double insulated copper cable( brown and black) each 44 metres | m | 88
5.3.1.1.10 | Lay in trench/duct, connect and test 1.5 mm2/2c pvc swa pvc copper cable (starter panel to borehole) | m | 20
5.3.1.1.11 | Lay in trench/duct, connect and test 10 mm2/4c armoured copper cable | m | 20
5.3.1.1.12 | Copper cable gland c/w lock-nut and shroud for 10 mm2/4 core pvc swa pvc copper cable. | Nr | 2
5.3.1.1.13 | Copper cable gland c/w lock-nut and shroud for 1.5 mm2/2 core pvc swa pvc copper cable. | Nr | 2
5.3.1.1.14 | Supply and install water-tight GS cable junction box of size 150x150x90mm depth, fabricated from 3 mm thick plate.. It shall have GS DIN plate fixed at the inside centre but raised by 10 mm from back side. 3 No. 10 amps and 5 No. 60 amps cable terminal blocks mounted on the plate, tough rubber cable grommets for 10 mm2/4c and 0.75 mm2 sc submerssible cable. | Nr | 1
5.3.1.1.15 | 22 Kw, 3 phase, 415 vac, soft starter panel including integral 3 phase surge arrestor unit. The cost shall be inclusive 10 mm2/4c armoured copper cable, cable glands etc for connection from starter panel to main switchgear. | SET | 1
5.3.1.1.16 | DN38x150 mmL GS threaded pipe piece (cable entry) | Nr | 1
5.3.1.1.17 | Supply and installation of Well Probe Sensor complete with well probe cable of size 0.75 mm² of 70 m (to be determined after test pumping). | SET | 1
TOTAL PAGE 1
5.3.1.1.18 | Supply, installation, testing and commissioning of Electro Magnetic Flow Meter, DN80, Qmax=80m3/hr, Qnom=40m3/hr, QT=8m3/hr and Qmin=1.2m3/hr, 2 battery power supply, IP 68, RS232 and RS 485 outputs. | Nr | 1
5.3.1.1.19 | Supply, installation, testing and commissioning of Hydrostatic Level Transmitter with integrated Pt 100 temperature sensor 0-700C, range from 1-100 mH2Og, acuracy + 0.175% FS BSL NLHR>4mH2O, +o.25%<4mH2O. | Nt | 1
5.3.1.1.20 | Installation Sundries
5.3.1.1.20a | ID220x4 mm Thick GS Borehole cap with welded DN100 GS pipe piece, welded DN38 GS slow bend for passage of 10mm2/4c cable, water level control electrodes cables and passage of OD25 mm pvc dipper pipe. | Nr | 1
5.3.1.1.20b | Boss white (200 gm tin) | pc | 2
5.3.1.1.20c | 500 mm plastic cable tie | Nr | 35
5.3.1.1.20d | 20 mm Wx9ML self bonding electrical tape (scotch 23) | ROLL | 2
5.3.1.1.20e | 12 mm Wx12 ML PTFE thread seal tape | ROLL | 10
5.3.1.1.20f | 20 mm high quality electrical pvc tape (Red, Yellow, Blue, Black) | ROLL | 4
5.3.1.1.20g | Stainless steel ferrules for 10mm2 cable | Nr | 4
5.3.1.1.20h | Stainless steel ferrules for 0.75 mm2 cable | Nr | 3
5.3.1.1.21 | Other Electro-mechanical Works - BH D2
5.3.1.1.21a | Preparation of all design technical and working drawings for the works for approval prior to commencement of installation of works as per the Specifications. | LS | 1
5.3.1.1.21b | Allow for all the builders works associated with all the electrical works that the contractor considers necessary to complete works | LS | 1
5.3.1.1.21c | Painting, varnishing and any other works necessary for making good all the disturbed areas as a result of the new electrical installations. | LS | 1
5.3.1.1.21d | Supply, installation, testing and commissioning of Amplified Pressure Transmitter with pressure range of 20 bar, over pressure safety of 50 bar, from SS material, and power supply 10<UCB<30 VDC and signal output 4-20 mA 2-wire system. | Nr | 1
5.3.1.1.21e | ID8x3 mm Thick GS tube c/w all necessary mounting fittings, bends etc enclosed in DN15 GS pipe for connection on GS rising main and laid in trenching/duct and connection on pressure switch, pressure gauge at the power supply control room. | m | 15
5.3.1.1.21f. | Adjustable Pressure switch in IP54 metal enclosure, with dual scale (Kg/cm2 and Bar), range 0 - 25 Kg/cm2 (0 - 25 Bar) connected to GS copper tube and fixed firmly on the wall by GS bracket. It shall have integral 2NO+2NC auxillary contacts rated 10 amps, 240 vac, stainless steel isolation ball valve. | Nr | 1
5.3.1.1.21g | High quality pressure gauge - (indoor mounting), with dual scale (Kg/cm2 and Bar).Range (0 - 30 Kg/cm2 )/(0 - 30 bar). It shall be c/w all fitting accessories for connecting on ID8x3mm GS tube. It shall be c/w stainless steel isolation ball valve. | Nr | 1
5.3.1.1.21h | Single orifice cast steel air valve c/w accessories for mounting on DN100 GS pipe. | Nr | 1
5.3.1.1.21i | Supply, installation, testing and commissioning of 24V DC Power Supply Unit, 500VAC Equipped with one input fuse, 187 – 264 VAC, 47 to 63 Hz,0°C….+45°C,≥ IP20. | Nr | 1
5.3.1.1.21j | Supply, installation and testing of Input /Output interface module (I/O), min. 4 analog inputs 0-10V, 0-20mA, 4-20mA programmable, min 2 digital inputs with frequency range 0-16 Hz. | Nr | 1
TOTAL PAGE 2
5.3.1.1.21k | Supply, installation and testing of Class 10 GPRS Modem, Dual-Band E-GSM/GPRS 900/1800 MHz,GPRS multi-slot class 10,1W@900 MHz,1W@ 1800 MHz,Control via AT commands, -200 C to +550C,RS 232 interface,TCP/IP protocol stack for M2M | Nr | 1
5.3.1.1.21l | Supply and installation of 1.5mm² armoured underground cable for the well probe. | m | 20
5.3.1.1.22 | Pressure Pipes and Fittings:
Modification of the connection between the new pump, the suction and the discharge pipes and fittings, and for corresponding concrete works.
5.3.1.1.22a | Disconnection, dismantling and disposal of old pipes, pipe fittings, valves, water meter. | LS | 1
Supply, delivery to Site, Install and Test:
5.3.1.1.22b | DN75x90o GS slow bend with a bore for pressure gauge | Nr | 1
5.3.1.1.22c | DN75 GS socket with bore for mounting air valve | Nr | 1
5.3.1.1.22d | DN100x1200 GS pipe piece (threaded at both ends) | Nr | 2
5.3.1.1.22e | DN100x300 GS pipe piece (threaded at both ends) | Nr | 1
5.3.1.1.22f | DN75x90o GS slow bend (threaded) | Nr | 3
5.3.1.1.22g | DN75 GS hex nipple | Nr | 4
5.3.1.1.22h | DN75 CS union | Nr | 3
5.3.1.1.22i | DN100xPN16 steel Non-slam Non-Return valve. | Nr | 1
5.3.1.1.22j | DN75xPN16 steel gate valve (threaded) c/w handwheel | Nr | 1
5.3.1.1.22k | DN100xPN16 steel gate valve c/w handwheel | Nr | 1
5.3.1.1.22l | DN100x250 mmL GS pipe piece | Nr | 2
5.3.1.1.22m | DN100x2000 mmL GS pipe piece. | Nr | 1
5.3.1.1.22n | DN100 steel Johnson coupling c/w rubber rings. | Nr | 3
5.3.1.1.22o | DN100x75 GS reducer. | Nr | 1
5.3.1.1.22p | DN75 steel Johnson coupling c/w rubber rings. | Nr | 1
5.3.1.1.22q | DN75x250 mmL adaptor GS pipe piece,flanged one end and plain the opposite end | Nr | 1
5.3.1.1.23r | DN100x250 mmL GS pipe piece one side flanged, the other side plain | Nr | 1
5.3.1.2 | INTER-CONNECTION OF BH D2 TO BH D1 RISING MAIN
5.3.1.2.01 | DN100 GS pipe laid, from BH D2 and connected to BH D3 rising main | m | 50
5.3.1.2.02 | DN100 Equal Yye Tee | Nr | 1
5.3.1.2.03 | DN100x300 mmL GS adaptor pipe piece. | Nr | 2
5.3.1.2.04 | DN100x50 mmL GS adaptor pipe piece. | Nr | 2
5.3.1.2.05 | Any other necessary item | LS | 1
5.3.1.3 | Removal Of Old Items and Trenching
5.3.1.3.01 | Excavate, expose and remove existing cables ( power control room to borehole). Trim the trenching to size 450 mmWx500 mm depth. Back fill to ground level after laying of cable. Cart away, dispose excess as advised. | m | 15
5.3.1.3.02 | Excavate, expose and remove a section of existing DN100 GS Borehole-rising main inter-connection pipe work. Trim the trenching to size 500 mmWx600 mm depth. Back fill to ground level after laying of pipe. Cart away, dispose excess as advised. | m | 60
TOTAL PAGE 3
BOREHOLE D3
ITEM | ITEM DESCRIPTION | UNIT | QTY | Rate(KES) | Amount(KES)
5.3.2 | Electro-Mechanical Works
Items below are given for assumed pump capacity, final specifications (e.g. cable thickness) and quantity are dependent on type of pump and pumping depths and have to be identified by the contractor after test pumping
SUPPLY, DELIVER TO SITE, INSTALL AND TEST:
NOTE:
5.3.2.1.01 | Submersible pump set of capacity 41m3/hr. of water against a total head of 180 metres directly coupled to 3 phase, 415 vac motor, with pump suction inlet at 62 metres below ground level. | Nr | 1
5.3.2.1.02 | Overheads and profits on item 5.3.2.1.01 as specified for Prime Cost sum items | %
5.3.2.1.03 | 16 mm2/4 core submersible pump flat cable | m | 65
5.3.2.1.04 | DN6x120 mmL stainless steel water level cotrol electrodes. | pair | 1
5.3.2.1.05 | OD25 class D uPVC dipper pipe | m | 62
5.3.2.1.06 | DN100 GS class C threaded water pipe. | m | 62
5.3.2.1.07 | DN100 GS steam sockets | Nr | 13
5.3.2.1.08 | DN100x300 mm long GS starter pipe | Nr | 1
5.3.2.1.09 | 0.75mm2 sc double insulated copper cable( brown and black) each 65 metres | m | 130
5.3.2.1.10 | Lay in trench/duct, connect and test 1.5 mm2/2c pvc swa pvc copper cable (starter panel to borehole) | m | 45
5.3.2.1.11 | Lay in trench/duct, connect and test 25 mm2/4c armoured copper cable | m | 45
5.3.2.1.12 | Copper cable gland c/w lock-nut and shroud for 25 mm2/4 core pvc swa pvc copper cable. | Nr | 2
5.3.2.1.13 | Copper cable gland c/w lock-nut and shroud for 1.5 mm2/2 core pvc swa pvc copper cable. | Nr | 2
5.3.2.1.14 | Supply and install water-tight GS cable junction box of size 150x150x90mm depth, fabricated from 3 mm thick plate.. It shall have GS DIN plate fixed at the inside centre but raised by 10 mm from back side. 3 No. 10 amps and 5 No. 80 amps cable terminal blocks mounted on the plate, tough rubber cable grommets for 16 mm2/4c and 0.75 mm2 sc submerssible cable. | Nr | 1
5.3.2.1.15 | 26 Kw, 3 phase, 415 vac, soft starter panel including integral 3 phase surge arrestor unit. The cost shall be inclusive 25 mm2/4c armoured copper cable, cable glands etc for connection from starter panel to main switchgear. | SET | 1
5.3.2.1.16 | DN38x150 mmL GS threaded pipe piece (cable entry) | Nr | 1
5.3.2.1.17 | Supply and installation of Well Probe Sensor complete with well probe cable of size 0.75 mm² of 70 m (to be determined after test pumping). | SET | 1
5.3.2.1.18 | Supply, installation, testing and commissioning of Electro Magnetic Flow Meter, DN80, Qmax=80m3/hr, Qnom=40m3/hr, QT=8m3/hr and Qmin=1.2m3/hr, 2 battery power supply, IP 68, RS232 and RS 485 outputs. | Nr | 1
TOTAL PAGE 4
5.3.2.1.19 | Supply, installation, testing and commissioning of Hydrostatic Level Transmitter with integrated Pt 100 temperature sensor 0-700C, range from 1-100 mH2Og, acuracy + 0.175% FS BSL NLHR>4mH2O, +o.25%<4mH2O. | Nr | 1
5.3.2.1.20 | Installation Sundries
5.3.2.1.20a | ID220x4 mm Thick GS Borehole cap with welded DN100 GS pipe piece, welded DN38 GS slow bend for passage of 10mm2/4c cable, water level control electrodes cables and passage of OD25 mm pvc dipper pipe. | Nr | 1
5.3.2.1.20b | Boss white (200 gm tin) | pc | 2
5.3.2.1.20c | 550 mm plastic cable tie | Nr | 30
5.3.2.1.20d | 20 mm Wx9ML self bonding electrical tape (scotch 23) | ROLL | 2
5.3.2.1.20e | 12 mm Wx12 ML PTFE thread seal tape | ROLL | 10
5.3.2.1.20f | 20 mm high quality electrical pvc tape (Red, Yellow, Blue, Black) | ROLL | 4
5.3.2.1.20g | Stainless steel ferrules for 10mm2 cable | Nr | 4
5.3.2.1.20h | Stainless steel ferrules for 0.75 mm2 cable | Nr | 3
5.3.2.1.21 | Other Electro-mechanical Works - BH D3
5.3.2.1.21a | Preparation of all design technical and working drawings for the works for approval prior to commencement of installation of works as per the Specifications. | LS | 1
5.3.2.1.21b | Allow for all the builders works associated with all the electrical works that the contractor considers necessary to complete works | LS | 1
5.3.2.1.21c | Painting, varnishing and any other works necessary for making good all the disturbed areas as a result of the new electrical installations. | LS | 1
5.3.2.1.21d | Supply, installation, testing and commissioning of Amplified Pressure Transmitter with pressure range of 20 bar, over pressure safety of 50 bar, from SS material, and power supply 10<UCB<30 VDC and signal output 4-20 mA 2-wire system. | Nr | 1
5.3.2.1.21e | ID8x3 mm Thick GS tube c/w all necessary mounting fittings, bends etc enclosed in DN15 GS pipe for connection on GS rising main and laid in trenching/duct and connection on pressure switch, pressure gauge at the power supply control room. | m | 15
5.3.2.1.21f | Adjustable Pressure switch in IP54 metal enclosure, with dual scale (Kg/cm2 and Bar), range 0 - 30 Kg/cm2 (0 - 30 Bar) connected to GS copper tube and fixed firmly on the wall by GS bracket. It shall have integral 2NO+2NC auxillary contacts rated 10 amps, 240 vac, stainless steel isolation ball valve. | Nr | 1
5.3.2.1.21g | High quality pressure gauge - (indoor mounting), with dual scale (Kg/cm2 and Bar).Range (0 - 35 Kg/cm2 )/(0 - 35 bar). It shall be c/w all fitting accessories for connecting on ID8x3mm GS tube. It shall be c/w stainless steel isolation ball valve. | Nr | 1
5.3.2.1.21h | Single orifice cast steel air valve c/w accessories for mounting on DN100 GS pipe. | Nr | 1
TOTAL PAGE 5
5.3.2.1.21i | Supply, installation, testing and commissioning of 24V DC Power Supply Unit, 500VAC Equipped with one input fuse, 187 – 264 VAC, 47 to 63 Hz,0°C….+45°C,≥ IP20. | Nr | 1
5.3.2.1.21j | Supply, installation and testing of Input /Output interface module (I/O), min. 4 analog inputs 0-10V, 0-20mA, 4-20mA programmable, min 2 digital inputs with frequency range 0-16 Hz. | Nr | 1
5.3.2.1.21k | Supply, installation and testing of Class 10 GPRS Modem, Dual-Band E-GSM/GPRS 900/1800 MHz,GPRS multi-slot class 10,1W@900 MHz,1W@ 1800 MHz,Control via AT commands, -200 C to +550C,RS 232 interface,TCP/IP protocol stack for M2M | Nr | 1
5.3.2.1.21l | Supply and installation of 1.5mm² armoured underground cable for the well probe. | m | 45
5.3.2.1.22 | Pressure Pipes and Fittings:
Modification of the connection between the new pump, the suction and the discharge pipes and fittings, and for corresponding concrete works.
5.3.2.1.22a | Disconnection, dismantling and disposal of old pipes, pipe fittings, valves, water meter. | LS | 1
Supply, delivery to Site, Install and Test:
5.3.2.1.22b | DN100x90o GS slow bend with a bore for pressure gauge | Nr | 1
5.3.2.1.22c | DN100 GS socket with bore for mounting air valve | Nr | 1
5.3.2.1.22d | DN100x1200 GS pipe piece (threaded at both ends) | Nr | 2
5.3.2.1.22e | DN100x300 GS pipe piece (threaded at both ends) | Nr | 1
5.3.2.1.22f | DN100x90o GS slow bend (threaded) | Nr | 3
5.3.2.1.22g | DN100 GS hex nipple | Nr | 4
5.3.2.1.22h | DN100xPN20 steel Non-slam Non-Return valve. | Nr | 1
5.3.2.1.22i | DN100xPN20 steel gate valve c/w handwheel | Nr | 1
5.3.2.1.22j | DN100x250 mmL GS pipe piece | Nr | 2
5.3.2.1.22k | DN100x2000 mmL GS pipe piece. | Nr | 1
5.3.2.1.22l | DN100 steel Johnson coupling c/w rubber rings. | Nr | 5
5.3.2.1.22m | DN100x250 mmL adaptor GS pipe piece,flanged one end and plain the opposite end | Nr | 4
5.3.2.3 | INTER-CONNECTION OF BH D2 TO BH D3 RISING MAIN
5.3.2.3.01 | DN100 GS Class C pipe laid, from BH D2 and connected to BH D3 rising main. | m | 50
5.3.2.3.02 | DN100 Equal Y-Tee | Nr | 1
5.3.2.3.03 | DN100x300 mmL GS adaptor pipe piece. | Nr | 3
5.3.2.3.04 | DN100x500 mmL GS adaptor pipe piece. | Nr | 3
5.3.2.3.05 | Any other necessry item | LS | 1
TOAL PAGE 6
5.3.3 | Removal Of Old Items and Trenching
5.3.3.01 | Excavate, expose and remove existing cables ( power control room to borehole). Trim the trenching to size 450 mmWx500 mm depth. Back fill to ground level after laying of cable. Cart away, dispose excess as advised. | m | 40
5.3.3.02 | Excavate, expose and remove a section of existing DN100 GS Borehole-rising main inter-connection pipe work. Trim the trenching to size 500 mmWx600 mm depth. Back fill to ground level after laying of pipe. Cart away, dispose excess as advised. | m | 5
5.3.3 | REHABILITATION OF MAINS POWER CONTROL SWITCHGEAR PANEL, ELECTRICAL WIRING OF SWITCHGEAR/OFFICE/SANITATION BUILDING AND FIRE FIGHTING EQUIPMENT
5.3.3.1 | MAINS POWER CONTROL SWITCHGEAR PANEL
5.3.3.1.01 | Open the mains power switchgear panel, carefully clean, dust and air blows the compartments. Tighten any loose, cables, bolts and nuts | Item | 1
5.3.3.1.02 | Install 3 phase, 415 vac surge divertor c/w protective mcbs and any other missing items. | LS | 1
5.3.3.2 | MAINS POWER CONTROL SWITCHGEAR/OFFICE BUILDING WIRING
5.3.3.2.01 | Remove the existing socket/lighting wiring, replace the defective sections of conduit | LS | 1
5.3.3.2.02 | Re-wire the lighting circuits using 1.5 mm2 single copper cables (Red=90 m, Black=70 m , Green =70 m). | m | 230
5.3.3.2.03 | Re-wire the sockets circuits using 2.5 mm2 single copper cables (Red= 60 m, Black=60 m , Green = 60 m) | m | 180
5.3.3.2.04 | 10 amps, I way 2 gang switch (IVY white, flush) as Mem, Crabtree or similar quality approved make. | Nr | 1
5.3.3.2.05 | 13 amps, 240 vac, single switched socket outlet (IVY White, flush) as Mem, Crabtree or similar quality approved make c/w stainless steel screws (ringmain circuit). | Nr | 4
5.3.3.2.06 | 36 wattsx1200 mmL single fluorescent lighting fitting, energy save, water tight (IP 20), metal body, corrossion resistant, power factor compensated, c/w tube, starter mounted on ceiling but 20 mm off the surface using 20 mm diam. GS coupler) | Nr | 2
5.3.3.2.07 | 20 wattsx300 mmL LED fluorescent lighting fitting (IP54), energy save, corrossion resistant, power factor compensated. | Nr | 4
5.3.3.2.08 | Masory earth rod chamber of internal size 250x250 x300 mmH extending 50 mm above the ground. It shall be constructed from 150x150x450 mmL masonry blocks (1:3:6). It shall be c/w 75 mm thick perforated cover (1:2:4). | Nr | 1
5.3.3.2.09 | D15x2.4 metre copper earth rod c/w clamp in a masonry chamber. | Nr | 1
5.3.3.2.10 | 25 mm2 sc copper cable laid trench and connected to earth rod and main switchgear panel earth bond tape. | m | 3
5.3.3.2.11 | 32 amps, TPN + E (5-pin), 415 vac, socket outet (smc) c/w isolator, base and screw top lid, wired using 6 mm2 sc copper cables in 32 mm diameter GS conduit. | Nr | 1
5.3.3.2.12 | 3 blade, adjustable slow speed (0-300 rpm), 240 vac ceiling mounted cooling fan c/w speed adjustable control unit completely wired (in GS conduit). | SET | 1
5.3.4 | Fire Fighting Equipment
5.3.4.01 | 5 Kg Class ABC Powder steel cylinder fire extinguisher, c/w pressure gauge wall mounting steel bracket , operating instructions and accessories, fully charged. | Nr | 2
5.3.5 | AC/DC POWER SUPPLY
| Floor stand supported, 240 ac, 2.5 amps/24 vdc, 20 amps continuosly rated converter fully protected (overload/short-circuit/reverse voltage and polarity etc c/w RJ45, RS232, RS485 ports, mcbs protected outputs to supply water meter, borehole water level measurement, rising main pressure measurement, PLC, Radio/Data Trans-Receiver Equipment. | SET | 1
TOTAL PAGE 7
TOTAL BHs D2, D3:- CARRIED TO BILLL 5 SUMMARY SHEET

## 5.4_BHE
PART 5.4 - Electro-Mechanical Works & Pipeworks Borehole E2 (Site-Repairs)
ITEM | DESCRIPTION | UNIT | QTY | Rate(KES) | Amount(KES)
5.4.1 | Electro-Mechanical Works:
Items below are given for assumed pump capacity, final specifications (e.g. cable thickness) and quantity are dependent on type of pump and pumping depths and have to be identified by the contractor after test pumping
5.4.1.1 | Remove Grundfos SP46-13 pump set c/w 42 metres of DN100 GI drop pipes. | LS | 1
SUPPLY, DELIVER TO SITE, INSTALL AND TEST:
5.4.1.2 | Submersible pump set of capacity 48 m3/hr. of water against a total head of 115 metres directly coupled to 3 phase, 415 vac motor, with pump suction inlet at 42 metres below ground level, c/w cable guard. | nr | 1
5.4.1.3 | Overheads and profits on item 5.4.1.2 as specified for Prime Cost sum items | %
5.4.1.4 | 10 mm2/4 core submersible pump flat cable | m | 45
5.4.1.5 | DN6x120 mmL stainless steel water level control electrodes. | pair | 1
5.4.1.6 | OD25 class D uPVC dipper pipe | m | 42
5.4.1.7 | DN100 GS class C threaded water pipe. | m | 42
5.4.1.8 | DN100 steel steam sockets | Nr | 11
5.4.1.9 | DN100x300 mm long GS starter pipe | Nr | 1
5.4.1.10 | 0.75mm2 sc double insulated copper cable( brown and black) each 45 metres | m | 90
5.4.1.11 | Lay in trench/duct, connect and test 1.5 mm2/2c pvc swa pvc copper cable | m | 20
5.4.1.12 | Lay in trench/duct, connect and test 10 mm2/4c armoured copper cable | m | 20
5.4.1.13 | Copper cable gland c/w lock-nut and shroud for 10m2/4 core pvc swa pvc copper cable. | Nr | 2
5.4.1.14 | Copper cable gland c/w lock-nut and shroud for 1.5 mm2/2 core pvc swa pvc copper cable | Nr | 2
5.4.1.15 | 22 Kw, 3 phase, 415 vac, soft starter panel including integral 3 phase surge arrestor unit. | SET | 1
5.4.1.16 | Masory earth rod chamber of internal size 250x250 x300 mmH extending 50 mm above the ground. It shall be constructed from 150x150x450 mmL masonry blocks (1:3:6). It shall be c/w 75 mm thick perforated cover (1:2:4). | Nr | 1
5.4.1.17 | D15x2.4 metre copper earth rod c/w clamp in a masonry chamber. | Nr | 1
5.4.1.18 | 35 mm2 sc copper cable (green) | m | 5
TOTAL PAGE 1
5.4.1.19 | Supply and install water-tight GS cable junction box of size 125x125x90mm depth, fabricated from 3 mm thick plate.. It shall have GS DIN plate fixed at the inside centre but raised by 10 mm from back side,. 3 No. 10 amps and 5 No. 60 amps cable terminal blocks mounted on the plate, tough rubber cable grommets for 10mm2/4c and 0.75 mm2 sc submerssible cables. | Nr | 1
5.4.1.20 | DN38x150 mmL GI threaded pipe piece (cable entry) | Nr | 1
5.4.1.21 | Supply and installation of Well Probe Sensor complete with well probe cable of size 0.75 mm² of 70 m (to be determined after test pumping). | SET | 1
5.4.1.22 | Supply, installation, testing and commissioning of Electro Magnetic Flow Meter, DN 80, Qmax=80m3/hr, Qnom=40m3/hr, QT=8m3/hr and Qmin=1.2m3/hr, 2 battery power supply, IP 68, RS232 and RS 485 outputs. | Nr | 1
5.4.1.23 | Supply, installation, testing and commissioning of Hydrostatic Level Transmitter with integrated Pt 100 temperature sensor 0-700C, range from 1-100 mH2Og, acuracy + 0.175% FS BSL NLHR>4mH2O, +o.25%<4mH2O. | Nr | 1
5.4.1.24 | INSTALLATION SUNDRIES
| ID320x7 mm Thick GS Borehole cap with welded DN100 GS pipe piece, welded DN38 GS slow bend for passage of 10 mm2/4c cable, water level control electrodes cables and passage of OD25 mm pvc dipper pipe. | Nr | 1
5.4.1.24b | Boss white (200 gm tin) | Pc | 3
5.4.1.24c | 550 mm plastic cable tie | Nr | 35
5.4.1.24d | 20 mm Wx9ML self bonding electrical tape (scotch 23) | ROLL | 2
5.4.1.24e | 12 mm Wx12 ML PTFE thread seal tape | ROLL | 15
5.4.1.24f | 20 mm high quality electrical pvc tape (Red, Yellow, Blue, Black) | ROLL | 4
5.4.1.24g | Stainless steel ferrules for 10 mm2 cable | Nr | 4
5.4.1.24h | Stainless steel ferrules for 0.75 mm2 cable | Nr | 2
New Mains Power Control Swichgear Panel and Switch gear/Office Building Wiring
5.4.2 | Mains Power Control Switchgear Panel
5.4.2.1 | Free standing, 250 amps, 3 phase, 415 vac, compact, compartmented, indoor, surface metal clad maiins power control panel (IP20), dust-proof, termite-proof, comprising of but not limited to the following, duly wired and labeled. It shall be constructed from gauge 16 spangled sheet steel of minimum thickness 1.75mm; | Nr | 1
5.4.2.2 | Kenya Power & Lighting Company CUT-OUTS chamber | Nr | 1
5.4.2.3 | 1xKPLC incommer Current transformers chamber | Nr | 1
5.4.2.4 | 1xKPLC metering equipment chamber incommer Current transformers chamber | Nr | 1
5.4.2.5 | 1x250 amps adjustable triple pole mccb (adjustable range: 0.7IN, 0.8IN, 0.9IN, 1.0IN set at 0.8IN where IN= rated current of mccb = 250 amps). | Nr | 1
TOTAL PAGE 2
5.4.2.6 | 1x20 Kvar, 3 phase, 415 vac, 5 step central automatic power capacitor correction bank c/w 100 amps TP supply mccb, contactors, fuses, programmable electronic PF controller.relay etc. | Nr | 1
5.4.2.7 | 1xsingle phase, 240 vac kWh energy registering meter (Client) | Nr | 1
5.4.2.8 | 4x260 amps high conductivity rectangular bare copper bus-bar conductors. | Nr | 1
5.4.2.9 | 2x100 amps, TP, 415 vac, mccbs, ICU =15 kA. Each in its own compartment (for Borehole E2 and 1 No. spare). | Nr | 1
5.4.2.10 | 2x63 amps, TP, 415 vac, mccbs, ICU =15 kA. Each in its own compartment. (Spares) | Nr | 1
5.4.2.11 | 1x3 phase, 415 vac surge divertor c/w protective mcbs on main 250 amps mccb terminals. | Nr | 1
5.4.2.12 | 2x100 amps,1phase, 240 vac class "A" mcbs (spare) | Nr | 1
5.4.2.13 | 1x Cooling fan rated 25 watts, 240 vac, 2800 rpm continuously rated installed on the side, 100 mm height from the bottom clw filter and termite-proof, dust-proof stainless steel protection D1.5 mm wiregauze. | Nr | 1
5.4.2.14 | 2x ventillation hole of size 150x100 mm installed on the top opposite sides, 50 mm below top c/w termite-proof, dust-proof filter and grid. | Nr | 1
5.4.2.15 | 1x3 phase, 240 vac network analyzer/recorder (voltage/current/kWh/Pf/Hz) resettable, as MCAplus, Circutor Smart or similar quality approved make with LED phase indicators (RED, YELLOW, BLUE) on front panel. | Nr | 1
5.4.2.16 | 3xAC ammeters range 0-300 amps c/w CTS. | Nr | 1
5.4.2.17 | 1xAC voltmeter c/w vss and protection mcbs. | Nr | 1
5.4.2.18 | 250 amps, 415 vac TPN manual changer-over switch c/w pilot indicator lights ( KPLC ON, KPLC LOAD ON, GENERATOR ON, GENERATOR LOAD ON etc). | Nr | 1
5.4.5.19 | 32 amps, TPN + E (5-pin), 415 vac, socket outet (smc) c/w isolator, base and screw top lid. | Nr | 1
5.4.2.20 | 25x3 mm thick copper strip bound along the switchgear panel length (earthing) | SET | 1
5.4.3 | Electrical Repairs of Mains Power Control Switchgear/Office Building
5.4.3.1 | Remove the existing socket/lighting wiring. | LS | 1
5.4.3.2 | 20 mm diam. GS conduit fixed on the walls and roof members. The cost shall be inclusive of tees, bends, circular boxes with covers, other necessary accessories | LM | 44
5.4.3.3 | 1.5 mm2 single copper cables (Red=70 m, Black=50 m , Green =50 m) laid in GS conduit and terminated at both ends. | LM | 170
5.4.3.4 | 2.5 mm2 single copper cables (Red=50 m, Black=50 m , Green =50 m) laid in GS conduit and terminated at both ends. | LM | 150
5.4.3.5 | 10 amps, I way 1 gang switch (smc) as Mem, Crabtree or similar quality approved make c/w box and ss screws | No | 3
TOTAL PAGE 3
5.4.3.6 | 13 amps, 240 vac, twin switched socket outlet (smc) as Mem, Crabtree or similar quality approved make c/w box stainless steel screws (ringmain circuit). | Nr | 2
5.4.3.7 | 36 wattsx1200 mmL single fluorescent lighting fitting, energy save, water tight (IP 20), metal body, corrossion resistant, power factor compensated, c/w tube, starter mounted on ceiling but 20 mm off the surface using 20 mm diam. GS coupler) | Nr | 2
5.4.3.8 | 20 wattsx300 mmL LED fluorescent lighting fitting (IP54), energy save, corrossion resistant, power factor compensated. | Nr | 4
5.4.3.9 | 100 watts, 240 vac, Opal white lighting fitting c/w 60 watts bulb | Nr | 1
5.4.3.10 | 1.5 mm2 single core copper cables wired in 20 mm diameter pvc conduit from consumer unit to fan speed control unit and fan terminals (red 12 m, black =12m, green=12 m). | m | 36
5.4.3.11 | 3 blade, adjustable slow speed (0-300 rpm), 240 vac ceiling mounted cooling fan c/w speed adjustable control unit completely wired (in conduit). | set | 1
5.4.3.12 | 35 mm2 sc copper cable laid trench and connected to earth rod and main switchgear panel earth bond tape | m | 3
5.4.3.13 | AC/DC POWER SUPPLY
5.4.3.13.01 | Floor stand supported, 240 ac, 2.5 amps/24 vdc, 20 amps continuosly rated converter fully protected (overload/short-circuit/reverse voltage and polarity etc c/w RJ45, RS232, RS485 ports, mcbs protected outputs to supply water meter, borehole water level measurement, rising main pressure measurement, PLC, Radio/Data Trans-Receiver Equipment. | SET | 1
5.4.4 | Fire Fighting Equipment
5.4.4.1 | 5 Kg Class ABC Powder steel cylinder fire extinguisher, c/w pressure gauge wall mounting steel bracket , operating instructions and accessories, fully charged. | Nr | 2
5.4.5 | Other Electro-Mechanical Works
5.4.5.1 | Improve lightning protection system | LS | 1
5.4.5.2 | Supply, installation, testing and commissioning of pole mounted 3 phase, 75 Kva,0.433 Kv/11 Kv ONAN transformer for the site. | Nr | 1
5.4.5.3 | Disconnection and handing over to the Employer the entire existing electrical installations | LS | 1
5.4.5.4 | Testing and commissioning of the incoming electricity supply and Main Low Voltage Switchboard | LS | 1
5.4.5.5 | Preparation of all design technical and working drawings for the works for approval prior to commencement of installation of works as per the Specifications. | LS | 1
5.4.5.6 | Allow for all the builders works associated with all the electrical works that the contractor considers necessary to complete works | LS | 1
5.4.5.7 | Painting, varnishing and any other works necessary for making good all the disturbed areas as a result of the new electrical installations | LS | 1
TOTAL PAGE 4
5.4.5.8 | Supply, installation, testing and commissioning of Amplified Pressure Transmitter with pressure range of 16 bar, over pressure safety of 50 bar, from SS material, and power supply 10<UCB<30 VDC and signal output 4-20 mA 2-wire system. | Nr | 1
5.4.5.9 | ID8x3 mm Thick GS tube c/w all necessary mounting fittings, bends etc enclosed in DN15 GI pipe for connection on GI rising main and laid in trenching/duct and connection on pressure switch, pressure gauge at the power supply control room. | m | 18
5.4.5.10 | Adjustable Pressure switch in IP54 metal enclosure, with dual scale (Kg/cm2 and Bar), range 0 - 20 Kg/cm2 (0-20 Bar) connected to GS copper tube and fixed firmly on the wall by GS bracket.. It shall have integral 2NO+2NC auxillary contacts rated 10 amps, 240 vac, stainless steel isolation ball valve. | Nr | 1
5.4.5.11 | High quality pressure gauge - (indoor mounting), with dual scale (Kg/cm2 and Bar).Range (0 - 20 Kg/cm2 )/(0 - 20 bar). It shall be c/w all fitting accessories for connecting on ID8x3mm GS tube. It shall be c/w stainless steel isolation ball valve. | Nr | 1
5.4.5.12 | Single orifice cast steel air valve c/w accessories for mounting on DN100 GS pipe | Nr | 1
5.4.5.13 | Supply, installation, testing and commissioning of 24V DC Power Supply Unit, 500VAC Equipped with one input fuse,187 – 264 VAC, 47 to 63 Hz,0°C….+45°C,≥ IP20, | Nr | 1
5.4.5.14 | Supply, installation and testing of Input / Output interface module (I/O), min. 4 analog inputs 0-10V, 0-20mA, 4-20mA programmable, min 2 digital inputs with frequency range 0-16 Hz | Nr | 1
5.4.5.15 | Supply, installation and testing of Class 10 GPRS Modem, Dual-Band E-GSM/GPRS 900/1800 MHz,GPRS multi-slot class 10,1W@900 MHz,1W@ 1800 MHz,Control via AT commands, -200 C to +550C,RS 232 interface,TCP/IP protocol stack for M2M | Nr | 1
5.4.5.16 | Supply and installation of 1.5mm² armoured underground cable for the well probe | m | 20
5.4.6 | Pressure Pipes and Fittings:
Modification of the connection between the new pump, the suction and the discharge pipes and fittings, and for corresponding concrete works.
5.4.6.1 | Disconnection, dismantling and disposal of old pipes, pipe fittings, valves, water meter. | LS | 1
TOTAL PAGE 5
Supply, delivery to Site, Install and Test:
5.4.6.2 | DN 100 mm, PN 16 bar non-slam, non-return valve. | Nr | 1
5.4.6.3 | DN 100 mm, PN 16 bar gate valve. | Nr | 1
5.4.6.4 | DN 100 mm, PN 16 bar Y-strainer | Nr | 1
5.4.6.5 | DN100x200 mmL GS pipe piece with bore for mounting an air valve. | Nr | 1
5.4.6.6 | DN100x1500 mmL GS pipe piece. | Nr | 1
5.4.6.7 | DN100x250 mmL GS pipe piece, flanged on one side and plain at the opposite end. | Nr | 4
5.4.6.8 | DN100x90o GS slow bend | Nr | 2
5.4.6.9 | DN100 GS socket | Nr | 4
5.4.6.10 | DN100 GS equal Tee | Nr | 1
5.4.6.11 | DN100 GI hex nipple | Nr | 4
5.4.6.12 | DN100 steel Johnson coupling c/w rubber rings. | Nr | 4
5.4.6.13 | 100mmWx5 mm thick rubber gasket | m | 2
5.4.6.14 | DN100x1200 mmL GS pipe piece threaded at both ends | Nr | 1
5.4.6.15 | DN100x2500 mmL double flanged GS pipe piece. | Nr | 1
5.4.6.16 | DN100x90o GS female threaded elbow. | Nr | 2
5.4.6.17 | DN100x6000 mmL GS pipe piece | Nr | 1
5.4.6.18 | DN100x2000 mmL GS pipe piece | Nr | 1
5.4.6.19 | Steel chequered cover plates of size 300 mmWx1000 mmLx10 mm Thick | Nr | 3
5.4.6.20 | Any other accessories required for the system | LS | 1
5.4.7 | Removal Of Old Items and Trenching
5.4.7.1 | Excavate, expose and remove existing cables ( power control room to borehole). Trim the trenching to size 450 mmWx500 mm depth. Back fill to ground level after laying of cable. Cart away, dispose excess as advised. | m | 15
5.4.7.2 | Break existing RC pipe support block. | Nr | 1
5.4.7.3 | Excavate to expose and remove a section of existing DN 100 GS Borehole-Rising main inter-connection pipe work. Trim the trenching to size 500 mmW 900 mm depth. Back fill to ground level after laying of cable. Cart away , dispose excess as advised. | m | 12
5.4.7.4 | Excavate cable trench of size 300 mmWx175 mm Depth floor slab (1:3:6) in the power control room (control power panel to starters and exit holes to boreholes. Straighten the sides and floor. Plaster the sides,place 25 mm thick screed (1:3). Apply nilo an all the surfaces and evel after laying of the pipe. Cart away , dispose debris as advised. | m | 3
TOTAL PAGE 6
TOTAL BH E:- CARRIED TO BILLL 5 SUMMARY SHEET

## 5.5_BHG1,G2
PART 5.5 - Electro-Mechanical Works & Pipeworks Borehole G1, G2 (Site-Repairs)
BOREHOLE G1
ITEM | DESCRIPTION | UNIT | QTY | Rate(KES) | Amount(KES)
5.5.1 | Electro-Mechanical Works:
Items below are given for assumed pump capacity, final specifications (e.g. cable thickness) and quantity are dependent on type of pump and pumping depths and have to be identified by the contractor after test pumping
5.5.1.01 | Remove Grundfos SP46-15 pump set c/w 48 metres of DN100 GI drop pipes. | LS | 1
SUPPLY, DELIVER TO SITE, INSTALL AND TEST:
NOTE:
5.5.1.02 | Submersible pump set of capacity 48 m3/hr. of water against a total head of 125 metres directly coupled to 3 phase, 415 vac motor, with pump suction inlet at 50 metres below ground level, c/w cable guard. | Nr | 1
5.5.1.03 | Overheads and profits on item 5.5.1.02 as specified for Prime Cost sum items | %
5.5.1.04 | 16 mm2/4 core submersible pump flat cable | m | 52
5.5.1.05 | DN6x120 mmL stainless steel water level control electrodes. | Pair | 1
5.5.1.06 | OD25 class D uPVC dipper pipe | m | 50
5.5.1.07 | DN100 GS class C threaded water pipe. | m | 50
5.5.1.08 | DN100 steel steam sockets | Nr | 12
5.5.1.09 | DN100x300 mm long GS starter pipe | Nr | 1
5.5.1.10 | 0.75mm2 sc double insulated copper cable( brown and black) each 45 metres | m | 104
5.5.1.11 | Lay in trench/duct, connect and test 1.5 mm2/2c pvc swa pvc copper cable | m | 25
5.5.1.12 | Lay in trench/duct, connect and test 16 mm2/4c armoured copper cable | m | 25
5.5.1.13 | Copper cable gland c/w lock-nut and shroud for 16m2/4 core pvc swa pvc copper cable. | Nr | 2
5.5.1.14 | Copper cable gland c/w lock-nut and shroud for 1.5 mm2/2 core pvc swa pvc copper cable | Nr | 2
5.5.1.15 | 22 Kw, 3 phase, 415 vac, soft starter panel including integral 3 phase surge arrestor unit. | SET | 1
5.5.1.16 | Masory earth rod chamber of internal size 250x250 x300 mmH extending 50 mm above the ground. It shall be constructed from 150x150x450 mmL masonry blocks (1:3:6). It shall be c/w 75 mm thick perforated cover (1:2:4). | Nr | 1
5.5.1.17 | D15x2.4 metre copper earth rod c/w clamp in a masonry chamber. | Nr | 1
5.5.1.18 | 35 mm2 sc copper cable (green) | m | 5
TOTAL PAGE 1
5.5.1.19 | Supply and install water-tight GS cable junction box of size 125x125x90mm depth, fabricated from 3 mm thick plate.. It shall have GS DIN plate fixed at the inside centre but raised by 10 mm from back side,. 3 No. 10 amps and 5 No. 80 amps cable terminal blocks mounted on the plate, tough rubber cable grommets for 16mm2/4c and 0.75 mm2 sc submerssible cables. | Nr | 1
5.5.1.20 | DN38x150 mmL GI threaded pipe piece (cable entry) | Nr | 1
5.5.1.21 | Supply and installation of Well Probe Sensor complete with well probe cable of size 0.75 mm² of 70 m (to be determined after test pumping). | SET | 1
5.5.1.22 | Supply, installation, testing and commissioning of Electro Magnetic Flow Meter, DN 80, Qmax=80m3/hr, Qnom=40m3/hr, QT=8m3/hr and Qmin=1.2m3/hr, 2 battery power supply, IP 68, RS232 and RS 485 outputs. | Nr | 1
5.5.1.23 | Supply, installation, testing and commissioning of Hydrostatic Level Transmitter with integrated Pt 100 temperature sensor 0-700C, range from 1-100 mH2Og, acuracy + 0.175% FS BSL NLHR>4mH2O, +o.25%<4mH2O. | Nr | 1
5.5.1.24 | INSTALLATION SUNDRIES
| ID320x7 mm Thick GS Borehole cap with welded DN100 GS pipe piece, welded DN38 GS slow bend for passage of 10 mm2/4c cable, water level control electrodes cables and passage of OD25 mm pvc dipper pipe. | Nr | 1
5.5.1.24b | Boss white (200 gm tin) | pc | 3
5.5.1.24c | 550 mm plastic cable tie | Nr | 35
5.5.1.24d | 20 mm Wx9ML self bonding electrical tape (scotch 23) | ROLL | 2
5.5.1.24e | 12 mm Wx12 ML PTFE thread seal tape | ROLL | 15
5.5.1.24f | 20 mm high quality electrical pvc tape (Red, Yellow, Blue, Black) | ROLL | 4
5.5.1.24g | Stainless steel ferrules for 16 mm2 cable | Nr | 4
5.5.1.24h | Stainless steel ferrules for 0.75 mm2 cable | Nr | 2
5.5.1.25 | Pressure Pipes and Fittings:
Modification of the connection between the new pump, the suction and the discharge pipes and fittings, and for corresponding concrete works.
5.5.1.25a | Disconnection, dismantling and disposal of old pipes, pipe fittings, valves, water meter. | LS | 1
TOTAL PAGE 2
Supply, delivery to Site, Install and Test:
5.5.1.25b | DN 100 mm, PN 16 bar non-slam, non-return valve. | Nr | 1
5.5.1.25c | DN 100 mm, PN 16 bar gate valve c/w handwheel. | Nr | 1
5.5.1.25d | DN 100 mm, PN 16 bar Y-strainer | Nr | 1
5.5.1.25e | DN100x200 mmL GS pipe piece theaded both ends with bore for mounting an air valve. | Nr | 1
5.5.1.25f | DN100x200 mmL GS adaptable pipe piece threaded both ends. | Nr | 1
5.5.1.25g | DN100x250 mmL GS pipe piece, flanged on one side and plain at the opposite end. | Nr | 3
5.5.1.25h | DN100x90o GS slow bend | Nr | 2
5.5.1.25i | DN100 GS socket theaded | Nr | 4
5.5.1.25j | DN100 GS equal Tee threaded | Nr | 6
5.5.1.25k | DN100 GS hex nipple | Nr | 4
5.5.1.25l | DN100 steel Johnson coupling c/w rubber rings. | Nr | 3
5.5.1.25m | 100mmWx5 mm thick rubber gasket | m | 2
5.5.1.25n | DN100x1000 mmL GS pipe piece threaded both ends. | Nr | 1
5.5.1.25o | DN100x90o GS female threaded elbow. | Nr | 2
5.5.1.25p | DN100x6000 mmL GS pipe piece threaaded both ends | Nr | 1
5.5.1.25q | DN100x3500 mmL GS pipe piece threaded both ends | Nr | 1
5.5.1.25r | DN100x250 mmL GS adaptable pipe piece. | Nr | 3
5.5.1.25s | Any other accessories required for the system | LS | 1
5.5.2 | Removal Of Old Items And Trenching
5.5.2.01 | Excavate, expose and remove existing cables ( power control room to borehole). Trim the trenching to size 450 mmWx500 mm depth. Back fill to ground level after laying of cable. Cart away, dispose excess as advised. | m | 20
5.5.2.02 | Break existing RC pipe support block. | Nr | 2
5.5.2.03 | Excavate to expose and remove a section of existing DN 100 GS Borehole-Rising main inter-connection pipe work. Trim the trenching to size 500 mmW900 mm depth. Back fill to ground level after laying of cable. Cart away , dispose excess as advised. | m | 12
5.5.2a | Other Electromechanical Works
5.5.2a.01 | Supply, installation, testing and commissioning of Amplified Pressure Transmitter with pressure range of 0 - 16 bar, over pressure safety of 50 bar, from SS material, and power supply 10<UCB<30 VDC and signal output 4-20 mA 2-wire system. | No. | 1
5.5.2a.02 | ID8x3 mm Thick stainless steel tube c/w all necessary mounting fittings, bends etc enclosed in DN20 GS pipe for connection on GS rising main and laid in trenching/duct and connection on pressure switch, pressure transmitter, pressure gauge at the power supply control room. | LM | 25
5.5.2a.03 | Adjustable Pressure switch in IP54 metal enclosure, with dual scale (Kg/cm2 and Bar), range 0 - 20 Kg/cm2 (0-20 Bar) connected to SS tube and fixed firmly on the wall by GS bracket. It shall have integral 2NO+2NC auxillary contacts rated 10 amps, 240 vac, stainless steel isolation ball valve. | No. | 1
5.5.2a.04 | High quality pressure gauge with dual scale (Kg/cm2 and Bar).Range (0 - 20 Kg/cm2 )/(0 - 20 bar). It shall be c/w all fitting accessories for connecting on ID8x3mm SS tube. It shall be c/w stainless steel isolation ball valve. | No. | 1
5.5.2a.05 | Single orifice cast steel air valve c/w accessories for mounting on DN100 GS pipe | No. | 1
5.5.2a.06 | Supply, installation, testing and commissioning of 24V DC Power Supply Unit, 500VAC Equipped with one input fuse,187 – 264 VAC, 47 to 63 Hz,0°C….+45°C,≥ IP20. | No. | 1
5.5.2a.07 | Supply, installation and testing of Input /Output interface module (I/O), min. 4 analog inputs 0-10V, 0-20mA, 4-20mA programmable, min 2 digital inputs with frequency range 0-16 Hz | No. | 1
5.5.2a.08 | Supply and installation of 1.5mm² armoured underground cable for the well probe. | LM | 25
TOTAL PAGE 3
BOREHOLE G2
ITEM | DESCRIPTION | UNIT | QTY | Rate(KES) | Amount(KES)
5.5.3 | Electro-Mechanical Works:
Items below are given for assumed pump capacity, final specifications (e.g. cable thickness) and quantity are dependent on type of pump and pumping depths and have to be identified by the contractor after test pumping
SUPPLY, DELIVER TO SITE, INSTALL AND TEST:
NOTE:
5.5.3.02 | Submersible pump set of capacity 48 m3/hr. of water against a total head of 125 metres directly coupled to 3 phase, 415 vac motor, with pump suction inlet at 50 metres below ground level, c/w cable guard. | Nr | 1
5.5.3.03 | Overheads and profits on item 5.5.3.02 as specified for Prime Cost sum items | %
5.5.3.04 | 16 mm2/4 core submersible pump flat cable | m | 52
5.5.3.05 | DN6x120 mmL stainless steel water level control electrodes. | Pair | 1
5.5.3.06 | OD25 class D uPVC dipper pipe | m | 50
5.5.3.07 | DN100 GS class C threaded water pipe. | m | 50
5.5.3.08 | DN100 steel steam sockets | Nr | 12
5.5.3.09 | DN100x300 mm long GS starter pipe | Nr | 1
5.5.3.10 | 0.75mm2 sc double insulated copper cable( brown and black) each 45 metres | m | 104
5.5.3.11 | Lay in trench/duct, connect and test 1.5 mm2/2c pvc swa pvc copper cable | m | 45
5.5.3.12 | Lay in trench/duct, connect and test 16 mm2/4c armoured copper cable | m | 45
5.5.3.13 | Copper cable gland c/w lock-nut and shroud for 16 m2/4 core pvc swa pvc copper cable. | Nr | 2
5.5.3.14 | Copper cable gland c/w lock-nut and shroud for 1.5 mm2/2 core pvc swa pvc copper cable | Nr | 2
5.5.3.15 | 22 Kw, 3 phase, 415 vac, soft starter panel including integral 3 phase surge arrestor unit. | SET | 1
5.5.3.16 | Masory earth rod chamber of internal size 250x250 x300 mmH extending 50 mm above the ground. It shall be constructed from 150x150x450 mmL masonry blocks (1:3:6). It shall be c/w 75 mm thick perforated cover (1:2:4). | Nr | 1
5.5.3.17 | D15x2.4 metre copper earth rod c/w clamp in a masonry chamber. | Nr | 1
5.5.3.18 | 35 mm2 sc copper cable (green) | m | 5
TOTAL PAGE 4
5.5.3.19 | Supply and install water-tight GS cable junction box of size 125x125x90mm depth, fabricated from 3 mm thick plate.. It shall have GS DIN plate fixed at the inside centre but raised by 10 mm from back side,. 3 No. 10 amps and 5 No. 80 amps cable terminal blocks mounted on the plate, tough rubber cable grommets for 16mm2/4c and 0.75 mm2 sc submerssible cables. | Nr | 1
5.5.3.20 | DN38x150 mmL GI threaded pipe piece (cable entry) | Nr | 1
5.5.3.21 | Supply and installation of Well Probe Sensor complete with well probe cable of size 0.75 mm² of 70 m (to be determined after test pumping). | SET | 1
5.5.3.22 | Supply, installation, testing and commissioning of Electro Magnetic Flow Meter, DN 80, Qmax=80m3/hr, Qnom=40m3/hr, QT=8m3/hr and Qmin=1.2m3/hr, 2 battery power supply, IP 68, RS232 and RS 485 outputs. | No | 1
5.5.1.23 | Supply, installation, testing and commissioning of Hydrostatic Level Transmitter with integrated Pt 100 temperature sensor 0-700C, range from 1-100 mH2Og, acuracy + 0.175% FS BSL NLHR>4mH2O, +o.25%<4mH2O. | Nr | 1
5.5.3.24 | INSTALLATION SUNDRIES
| ID220x4 mm Thick GS Borehole cap with welded DN100 GS pipe piece, welded DN38 GS slow bend for passage of 16 mm2/4c cable, water level control electrodes cables and passage of OD25 mm pvc dipper pipe. | Nr | 1
5.5.3.24b | Boss white (200 gm tin) | pc | 3
5.5.3.24c | 550 mm plastic cable tie | Nr | 35
5.5.3.24d | 20 mm Wx9ML self bonding electrical tape (scotch 23) | ROLL | 2
5.5.3.24e | 12 mm Wx12 ML PTFE thread seal tape | ROLL | 15
5.5.3.24f | 20 mm high quality electrical pvc tape (Red, Yellow, Blue, Black) | ROLL | 4
5.5.3.24g | Stainless steel ferrules for 16 mm2 cable | Nr | 4
5.5.3.24h | Stainless steel ferrules for 0.75 mm2 cable | Nr | 2
5.5.3.25 | Pressure Pipes and Fittings:
Modification of the connection between the new pump, the suction and the discharge pipes and fittings, and for corresponding concrete works.
5.5.3.25a | Disconnection, dismantling and disposal of old pipes, pipe fittings, valves, water meter. | LS | 1
Supply, delivery to Site, Install and Test:
5.5.3.25b | DN 100 mm, PN 16 bar non-slam, non-return valve. | Nr | 1
5.5.3.25c | DN 100 mm, PN 16 bar gate valve c/w handwheel. | Nr | 1
5.5.3.25d | DN 100 mm, PN 16 bar Y-strainer | Nr | 1
5.5.3.25e | DN100x200 mmL GS pipe piece theaded both ends with bore for mounting an air valve. | Nr | 1
5.5.3.25f | DN100x200 mmL GS adaptable pipe piece threaded both ends. | Nr | 1
5.5.3.25g | DN100x250 mmL GS pipe piece, flanged on one side and plain at the opposite end. | Nr | 3
5.5.3.25h | DN100x90o GS slow bend | Nr | 2
5.5.3.25i | DN100 GS socket theaded | Nr | 4
5.5.3.25j | DN100 GS equal Tee threaded | Nr | 6
5.5.3.25k | DN100 GS hex nipple | Nr | 4
5.5.3.25l | DN100 steel Johnson coupling c/w rubber rings. | Nr | 3
5.5.3.25m | 100mmWx5 mm thick rubber gasket | m | 2
5.5.3.25n | DN100x1000 mmL GS pipe piece threaded both ends. | Nr | 1
5.5.3.25o | DN100x90o GS female threaded elbow. | Nr | 2
5.5.3.25p | DN100x6000 mmL GS pipe piece threaaded both ends | Nr | 1
5.5.3.25q | DN100x3500 mmL GS pipe piece threaded both ends | Nr | 1
5.5.3.25r | DN100x250 mmL GS adaptable pipe piece. | Nr | 3
5.5.3.25s | Any other accessories required for the system | LS | 1
| TOTAL PAGE 5 |  |  |  | 0
5.5.4 | Removal Of Old Items and Trenching
5.5.4.01 | Excavate, expose and remove existing cables ( power control room to borehole). Trim the trenching to size 450 mmWx500 mm depth. Back fill to ground level after laying of cable. Cart away, dispose excess as advised. | m | 40
5.5.4.02 | Break existing RC pipe support block. | No | 1
5.5.4.03 | Excavate to expose and remove a section of existing DN 100 GS Borehole-Rising main inter-connection pipe work. Trim the trenching to size 500 mmW900 mm depth. Back fill to ground level after laying of cable. Cart away , dispose excess as advised. | m | 12
5.5.5 | New Mains Power Control Swichgear Panel and Switch gear/Office Building Wiring
5.5.5.1 | Mains Power Control Switchgear Panel
5.5.5.1.01 | Open the mains power switchgear panel, carefully clean, dust and air blows the compartments. Tighten any loose, cables, bolts and nuts. | LS | 1
5.5.5.1.02 | Supply, install, test 3 phase, 415 vac surge divertor c/w protective mcbs. | Nr | 1
5.5.5.1.03 | Supply, install panel cooling fan rated 18 watts, 240 vac, 0.1 amps, 2860 rpm | Nr | 1
5.5.5.1.04 | Supply and install any other missing items | LS | 1
5.5.5.2 | Electrical Repairs of Mains Power Control Switchgear/Office Building
5.5.5.1.01 | Remove the existing socket/lighting wiring. | LS | 1
5.5.5.1.02 | 20 mm diam. GS conduit fixed on the walls and roof members. The cost shall be inclusive of tees, bends, circular boxes with covers, other necessary accessories | m | 44
5.5.5.1.03 | 1.5 mm2 single copper cables (Red=70 m, Black=50 m , Green =50 m) laid in GS conduit and terminated at both ends. | m | 170
5.5.5.1.04 | 2.5 mm2 single copper cables (Red=50 m, Black=50 m , Green =50 m) laid in GS conduit and terminated at both ends. | m | 150
5.5.5.1.05 | 10 amps, I way 1 gang switch (smc) as Mem, Crabtree or similar quality approved make c/w box and ss screws | Nr | 3
5.5.5.1.06 | 13 amps, 240 vac, twin switched socket outlet (smc) as Mem, Crabtree or similar quality approved make c/w box stainless steel screws (ringmain circuit). | Nr | 2
5.5.5.1.07 | 36 wattsx1200 mmL single fluorescent lighting fitting, energy save, water tight (IP 20), metal body, corrossion resistant, power factor compensated, c/w tube, starter mounted on ceiling but 20 mm off the surface using 20 mm diam. GS coupler) | Nr | 2
5.5.5.1.08 | 20 wattsx300 mmL LED fluorescent lighting fitting (IP54), energy save, corrossion resistant, power factor compensated. | Nr | 4
5.5.5.1.09 | 100 watts, 240 vac, Opal white lighting fitting c/w 60 watts bulb | Nr | 1
5.5.5.1.01 | 1.5 mm2 single core copper cables wired in 20 mm diameter pvc conduit from consumer unit to fan speed control unit and fan terminals (red 12 m, black =12m, green=12 m). | m | 36
5.5.5.1.10 | 3 blade, adjustable slow speed (0-300 rpm), 240 vac ceiling mounted cooling fan c/w speed adjustable control unit completely wired (in conduit). | set | 1
5.5.5.1.11 | 35 mm2 sc copper cable laid trench and connected to earth rod and main switchgear panel earth bond tape | m | 3
5.5.5.1.12 | 32 amps, TPN + E (5-pin), 415 vac, socket outet (smc) c/w isolator, base and screw top lid, wired using 6 mm2 sc copper cables in 32 mm diameter GS conduit. | No. | 1
5.5.5.1.13 | AC/DC POWER SUPPLY
5.5.5.1.13.01 | Floor stand supported, 240 ac, 2.5 amps/24 vdc, 20 amps continuosly rated converter fully protected (overload/short-circuit/reverse voltage and polarity etc c/w RJ45, RS232, RS485 ports, mcbs protected outputs to supply water meter, borehole water level measurement, rising main pressure measurement, PLC, Radio/Data Trans-Receiver Equipment. | SET | 1
5.5.6 | Fire Fighting Equipment
5.5.6.01 | 5 Kg Class ABC Powder steel cylinder fire extinguisher, c/w pressure gauge wall mounting steel bracket , operating instructions and accessories, fully charged. | Nr | 2
5.5.7 | Other Electro-Mechanical Works
5.5.7.01 | Improve lightning protection system | set | 2
5.5.7.02 | Supply, installation, testing and commissioning of pole mounted 3 phase, 75 Kva,0.433 Kv/11 Kv ONAN transformer for the site. | Nr | 1
TOTAL PAGE 6
5.5.7.03 | Testing and commissioning of the incoming electricity supply and Main Low Voltage Switchboard | LS | 1
5.5.7.04 | Preparation of all design technical and working drawings for the works for approval prior to commencement of installation of works as per the Specifications. | LS | 1
5.5.7.05 | Allow for all the builders works associated with all the electrical works that the contractor considers necessary to complete works | LS | 1
5.5.7.06 | Painting, varnishing and any other works necessary for making good all the disturbed areas as a result of the new electrical installations | LS | 1
5.5.7.07 | Supply, installation, testing and commissioning of Amplified Pressure Transmitter with pressure range of 16 bar, over pressure safety of 50 bar, from SS material, and power supply 10<UCB<30 VDC and signal output 4-20 mA 2-wire system. | Nr | 1
5.5.7.08 | ID8x3 mm Thick GS tube c/w all necessary mounting fittings, bends etc enclosed in DN15 GI pipe for connection on GI rising main and laid in trenching/duct and connection on pressure switch, pressure gauge at the power supply control room. | m | 45
5.5.7.09 | Adjustable Pressure switch in IP54 metal enclosure, with dual scale (Kg/cm2 and Bar), range 0 - 20 Kg/cm2 (0-20 Bar) connected to GS copper tube and fixed firmly on the wall by GS bracket.. It shall have integral 2NO+2NC auxillary contacts rated 10 amps, 240 vac, stainless steel isolation ball valve. | Nr | 1
5.5.7.10 | High quality pressure gauge with dual scale (Kg/cm2 and Bar).Range (0 - 20 Kg/cm2 )/(0 - 20 bar). It shall be c/w all fitting accessories for connecting on ID8x3mm GS tube. It shall be c/w stainless steel isolation ball valve. | Nr | 1
5.5.7.11 | Single orifice cast steel air valve c/w accessories for mounting on DN100 GS pipe | Nr | 1
5.5.7.12 | Supply, installation, testing and commissioning of 24V DC Power Supply Unit, 500VAC Equipped with one input fuse,187 – 264 VAC, 47 to 63 Hz,0°C….+45°C,≥ IP20, | Nr | 1
5.5.7.13 | Supply, installation and testing of Input / Output interface module (I/O), min. 4 analog inputs 0-10V, 0-20mA, 4-20mA programmable, min 2 digital inputs with frequency range 0-16 Hz | Nr | 1
5.5.7.14 | Supply and installation of 1.5mm² armoured underground cable for the well probe | m | 45
Total Page 7
TOTAL BHs G1 & G2:- CARRIED TO BILLL 5 SUMMARY SHEET

## 5.6_BH1
PART 5.6 - Electro-Mechanical Works & Pipeworks (Site-Repairs)
5.6.1 Tiwi Borehole No. 1
ITEM | DESCRIPTION | UNIT | QTY | Rate(KES) | Amount(KES)
5.6.1 | Electro-Mechanical Works:
Items below are given for assumed pump capacity, final specifications (e.g. cable thickness) and quantity are dependent on type of pump and pumping depths and have to be identified by the contractor after test pumping
5.6.1.1 | Remove pump set and 70 metres of DN100 GI drop pipes. | LS | 1
SUPPLY, DELIVER TO SITE, INSTALL AND TEST:
5.6.1.2 | Submersible pump set of capacity 50 m3/hr. of water against a total head of 125 metres directly coupled to 3 phase, 415 vac motor, with pump suction inlet at 70 metres below ground level. | Nr | 1
5.6.1.3 | Overheads and profits on item 5.6.1.2 as specified for Prime Cost sum items | %
5.6.1.4 | 16 mm2/4 core submersible pump flat cable | m | 75
5.6.1.5 | DN6x120 mmL stainless steel water level control electrodes. | Pair | 1
5.6.1.6 | OD25 class D uPVC dipper pipe | m | 75
5.6.1.7 | DN100 GI class C threaded water pipe. | m | 72
5.6.1.8 | DN100 GI steam sockets | Nr | 17
5.6.1.9 | DN75x300 mm long GI starter pipe | Nr | 1
5.6.1.10 | DN100x75 GI reducer (female threaded) | Nr | 1
5.6.1.11 | 0.75mm2 sc double insulated copper cable( brown and black) each 75 metres | m | 150
5.6.1.12 | Lay in trench/duct, connect and test 1.5 mm2/2c pvc swa pvc copper cable | m | 30
5.6.1.13 | Lay in trench/duct, connect and test 16 mm2/4c armoured copper cable | m | 30
5.6.1.14 | Copper cable gland c/w lock-nut and shroud for 16 mm2/4 core pvc swa pvc copper cable. | Nr | 2
5.6.1.15 | Copper cable gland c/w lock-nut and shroud for 1.5 mm2/2 core pvc swa pvc copper cable | Nr | 2
5.5.1.16 | 22 Kw, 3 phase, 415 vac, soft starter panel including integral 3 phase surge arrestor unit. | SET | 1
5.6.1.17 | Masory earth rod chamber of internal size 250x250 x300 mmH extending 50 mm above the ground. It shall be constructed from 150x150x450 mmL masonry blocks (1:3:6). It shall be c/w 75 mm thick perforated cover (1:2:4). | Nr | 1
5.6.1.18 | D15x2.4 metre copper earth rod c/w clamp in a masonry chamber. | Nr | 1
5.6.1.19 | 35 mm2 sc copper cable (green) | m | 5
5.6.1.20 | Supply and install water-tight GS cable junction box of size 125x125x90mm depth, fabricated from 3 mm thick plate.. It shall have GS DIN plate fixed at the inside centre but raised by 10 mm from back side,. 3 No. 10 amps and 5 No. 60 amps cable terminal blocks mounted on the plate, tough rubber cable grommets for 16mm2/4c and 0.75 mm2 sc submerssible cables. | Nr | 1
5.6.1.21 | DN38x150 mmL GI threaded pipe piece (cable entry) | Nr | 1
5.6.1.22 | Supply and installation of Well Probe Sensor complete with well probe cable of size 0.75 mm² of 70 m (to be determined after test pumping). | SET | 1
TOTAL PAGE 1
5.6.1.23 | Supply, installation, testing and commissioning of Electro Magnetic Flow Meter, DN 80, Qmax=80m3/hr, Qnom=40m3/hr, QT=8m3/hr and Qmin=1.2m3/hr, 2 battery power supply, IP 68, RS232 and RS 485 outputs. | Nr | 1
5.6.1.24 | Supply, installation, testing and commissioning of Hydrostatic Level Transmitter with integrated Pt 100 temperature sensor 0-700C, range from 1-100 mH2Og, acuracy + 0.175% FS BSL NLHR>4mH2O, +o.25%<4mH2O. | Nr | 1
5.6.1.25 | INSTALLATION SUNDRIES
5.6.1.25a | ID320x7 mm Thick GS Borehole cap with welded DN100 GI pipe piece, welded DN44 GI slow bend for passage of 25mm2/4c cable, water level control electrodes cables and passage of OD25 mm pvc dipper pipe. | Nr | 1
5.6.1.25b | Boss white (200 gm tin) | Pc | 1
5.6.1.25c | 550 mm plastic cable tie | Nr | 45
5.6.1.25d | 20 mm Wx9ML self bonding electrical tape (scotch 23) | Roll | 2
5.6.1.25e | 12 mm Wx12 ML PTFE thread seal tape | Roll | 15
5.6.1.25f | 20 mm high quality electrical pvc tape (Red, Yellow, Blue, Black) | Roll | 4
5.6.1.25g | Stainless steel ferrules for 16 mm2 cable | Nr | 4
New Mains Power Control Swichgear Panel and Switch gear/Office Building Wiring
5.6.2 | Mains Power Control Switchgear Panel
5.6.2.1 | Free standing, 250 amps, 3 phase, 415 vac, compact, compartmented, indoor, surface metal clad maiins power control panel (IP20), dust-proof, termite-proof, comprising of but not limited to the following, duly wired and labeled. It shall be constructed from gauge 16 spangled sheet steel of minimum thickness 1.75mm; | Nr | 1
5.6.2.2 | Kenya Power & Lighting Company CUT-OUTS chamber | Nr | 1
5.6.2.3 | 1xKPLC incommer Current transformers chamber | Nr | 1
5.6.2.4 | 1xKPLC metering equipment chamber incommer Current transformers chamber | Nr | 1
5.6.2.5 | 1x250 amps adjustable triple pole mccb (adjustable range: 0.7IN, 0.8IN, 0.9IN, 1.0IN set at 0.8IN where IN= rated current of mccb = 250 amps). | Nr | 1
5.6.2.6 | 1x25 Kvar, 3 phase, 415 vac, 5 step central automatic power capacitor correction bank c/w 100 amps TP supply mccb, contactors, fuses, programmable electronic PF controller.relay. 154 µF/phase etc. | Nr | 1
5.6.2.7 | 1xsingle phase, 240 vac kWh energy registering meter (Client) | Nr | 1
5.6.2.8 | 4x260 amps high conductivity rectangular bare copper bus-bar conductors. | Nr | 1
5.6.2.9 | 2x125 amps, TP, 415 vac, mccbs, ICU =15 kA. Each in its own compartment (for Borehole No. 1 and 1 No. spare). | Nr | 1
5.6.2.10 | 1x63 amps, TP, 415 vac, mccbs, ICU =15 kA. Each in its own cmpartment. (Spares) | Nr | 1
5.6.2.11 | 1x3 phase, 415 vac surge divertor c/w protective mcbs on main 250 amps mccb terminals. | Nr | 1
5.6.2.12 | 2x100 amps,1phase, 240 vac class "A" mcbs (staff houses) | Nr | 1
5.6.2.13 | 1x Cooling fan rated 25 watts, 240 vac, 2800 rpm continuously rated installed on the side, 100 mm height from the bottom clw filter and termite-proof, dust-proof stainless steel protection D1.5 mm wiregauze. | Nr | 1
TOTAL PAGE 2
5.6.2.14 | 2x ventillation hole of size 150x100 mm installed on the top opposite sides, 50 mm below top c/w termite-proof, dust-proof filter and grid. | Nr | 1
5.6.2.15 | 1x3 phase, 240 vac network analyzer/recorder (voltage/current/kWh/Pf/Hz) resettable, as MCAplus, Circutor Smart or similar quality approved make with LED phase indicators (RED, YELLOW, BLUE) on front panel. | Nr | 1
5.6.2.16 | 100 amps, 6 way, 1 phase, 240 vac DIN distribution board; c/w; 2 No. 10 amps, 1 pole, 240 vac class "A" mcbs, 3 No. 20 amps, 1 pole class "A" mcbs, 1 No. Blanking plate. | Nr | 1
5.6.2.17 | 250 amps, 415 vac TPN manual changer-over switch c/w pilot indicator lights ( KPLC ON, KPLC LOAD ON, GENERATOR ON, GENERATOR LOAD ON etc). | Nr | 1
5.6.2.18 | 3xAC ammeters range 0-300 amps c/w CTS. | Nr | 1
5.6.2.19 | 1xAC voltmeter (0-500 vac) c/w vss and protection mcbs. | Nr | 1
5.6.5.20 | 32 amps, TPN + E (5-pin), 415 vac, socket outet (smc) c/w isolator, base and screw top lid. | Nr | 1
5.6.2.21 | 25x3 mm thick copper strip bound along the switchgear panel length (earthing) | SET | 1
5.6.3 | Electrical Repairs of Mains Power Control Switchgear/Office Building
5.6.3.1 | Remove the existing socket/lighting wiring, replace the defective sections of conduit | LS | 1
5.6.3.2 | Re-wire the lighting circuits using 1.5 mm2 single copper cables (Red=80 m, Black=50 m , Green =50 m). | m | 180
5.6.3.3 | Re-wire the sockets circuits using 2.5 mm2 single copper cables (Red=25m, Black=25 m , Green =25 m) | m | 180
5.6.3.4 | 6 amps, I way 1 gang switch (IVY white, flush) as Mem, Crabtree or similar quality approved make, c/w stsinless steel screws. | Nr | 2
5.6.3.5 | 10 amps, I way 2 gang switch (IVY white, flush) as Mem, Crabtree or similar quality approved make. | Nr | 1
5.6.3.6 | 13 amps, 240 vac, twin switched socket outlet (IVY White, flush) as Mem, Crabtree or similar quality approved make c/w stainless steel screws (ringmain circuit). | Nr | 3
5.6.3.7 | 36 wattsx1200 mmL single fluorescent lighting fitting, energy save, water tight (IP 20), metal body, corrossion resistant, power factor compensated, c/w tube, starter mounted on ceiling but 20 mm off the surface using 20 mm diam. GS coupler) | Nr | 2
5.6.3.8 | 20 wattsx300 mmL LED fluorescent lighting fitting (IP54), energy save, corrossion resistant, power factor compensated. | Nr | 4
5.6.3.9 | 100 watts, 240 vac, Opal white lighting fitting c/w 60 watts bulb | Nr | 1
5.6.3.10 | 1.5 mm2 single core copper cables wired in 20 mm diameter pvc conduit from consumer unit to fan speed control unit and fan terminals (red 12 m, black =12m, green=12 m). | m | 36
5.6.3.11 | 3 blade, adjustable slow speed (0-300 rpm), 240 vac ceiling mounted cooling fan c/w speed adjustable control unit completely wired (in conduit). | set | 1
5.6.3.12 | 35 mm2 sc copper cable laid trench and connected to earth rod and main switchgear panel earth bond tape | Nr | 3
5.6.3.13 | AC/DC POWER SUPPLY
5.6.3.13.01 | Floor stand supported, 240 ac, 2.5 amps/24 vdc, 20 amps continuosly rated converter fully protected (overload/short-circuit/reverse voltage and polarity etc) c/w RJ45, RS232, RS485 ports, mcbs protected outputs to supply water meter, borehole water level measurement, rising main pressure measurement, PLC, Radio/Data Trans-Receiver Equipment. | SET | 1
5.6.3.14 | FIRE FIGHTING EQUIPMENT
5.6.3.14.01 | 5 Kg Class ABC Powder steel cylinder fire extinguisher, c/w pressure gauge wall mounting steel bracket , operating instructions and accessories, fully charged. | Nr | 2
TOTAL PAGE 3
5.6.4 | MODIFICATION OF EXISTING BOREOLE No. 1 STARTER PANNEL
5.6.4.1 | Fix 3 phase, 415 vac surge divertor c/w protective mcbs on incomer mccb terminals | Nr | 1
5.6.4.2 | Rewire neatly and label the starter panel. | LS | 1
5.6.5 | Other Electro-Mechanical Works
5.6.5.1 | Improve lightning protection system | LS | 1
5.6.5.2 | Supply, installation, testing and commissioning of pole mounted 3 phase, 75 Kva,0.433 Kv/11 Kv ONAN transformer for the site. | Nr | 1
5.6.5.3 | Disconnection and handing over to the Employer the entire existing electrical installations | LS | 1
5.6.5.4 | Testing and commissioning of the incoming electricity supply and Main Low Voltage Switchboard | LS | 1
5.6.5.5 | Preparation of all design technical and working drawings for the works for approval prior to commencement of installation of works as per the Specifications. | LS | 1
5.6.5.6 | Allow for all the builders works associated with all the electrical works that the contractor considers necessary to complete works | LS | 1
5.6.5.7 | Painting, varnishing and any other works necessary for making good all the disturbed areas as a result of the new electrical installations | LS | 1
5.6.5.8 | Supply, installation, testing and commissioning of Amplified Pressure Transmitter with pressure range of 16 bar, over pressure safety of 50 bar, from SS material, and power supply 10<UCB<30 VDC and signal output 4-20 mA 2-wire system. | Nr | 1
5.6.5.9 | ID8x3 mm Thick GS tube c/w all necessary mounting fittings, bends etc enclosed in DN15 GI pipe for connection on GI rising main and laid in trenching/duct and connection on pressure switch, pressure gauge at the power supply control room. | m | 25
5.6.5.10 | Adjustable Pressure switch in IP54 metal enclosure, with dual scale (Kg/cm2 and Bar), range 0 - 20 Kg/cm2 (0-20 Bar) connected to GS copper tube and fixed firmly on the wall by GS bracket.. It shall have integral 2NO+2NC auxillary contacts rated 10 amps, 240 vac, stainless steel isolation ball valve. | nr | 1
5.6.5.11 | High quality pressure gauge - IP54 (indoor mounting), with dual scale (Kg/cm2 and Bar).Range (0 - 20 Kg/cm2 )/(0 - 20 bar). It shall be c/w all fitting accessories for connecting on ID8x3mm GS tube. It shall be c/w stainless steel isolation ball valve. | Nr | 1
5.6.5.12 | Single orifice cast steel air valve c/w accessories for mounting on DN100 GI pipe | Nr | 1
5.6.5.213 | Supply, installation, testing and commissioning of 24V DC Power Supply Unit, 500VAC Equipped with one input fuse,187 – 264 VAC, 47 to 63 Hz,0°C….+45°C,≥ IP20, | Nr | 1
5.6.5.14 | Supply, installation and testing of Input / Output interface module (I/O), min. 4 analog inputs 0-10V, 0-20mA, 4-20mA programmable, min 2 digital inputs with frequency range 0-16 Hz | Nr | 1
5.6.5.15 | Supply, installation and testing of Class 10 GPRS Modem, Dual-Band E-GSM/GPRS 900/1800 MHz,GPRS multi-slot class 10,1W@900 MHz,1W@ 1800 MHz,Control via AT commands, -200 C to +550C,RS 232 interface,TCP/IP protocol stack for M2M | Nr | 1
5.6.5.16 | Supply and installation of 1.5mm² armoured underground cable for the well probe | m | 30
5.6.5.17 | Preparation of all design technical and working drawings for the works for approval prior to commencement of installation on works as per the Specifications | LS | 1
5.6.5.18 | Allow for all the builders works associated with all the electrical works that the contractor considers necessary to complete works | LS | 1
TOTAL PAGE 4
5.6.6 | Pressure Pipes and Fittings:
Modification of the connection between the new pump, the suction and the discharge pipes and fittings, and for corresponding concrete works.
5.6.6.1 | Disconnection, dismantling and disposal of old pipes, pipe fittings, valves, water meter. | LS | 1
Supply, delivery to Site, Install and Test:
NOTE: i). All Valves, pipes, pipe fittings, water meter shall be new.
ii). Unless otherwise stated, valves, pipes, pipe fittings, water
meter shall be double flanged, drilled and supplied c/w high
tensile strength stainless steel bolts, nuts and washers.
iii). Cutting and adjustment of pipework on site to fit.
5.6.6.2 | DN 100 mm, PN 16 bar non-slam, non-return valve. | Nr | 1
5.6.6.3 | DN 100 mm, PN 16 bar gate valve. | Nr | 1
5.6.6.4 | DN 100 mm, PN 16 bar Y-strainer | Nr | 1
5.6.6.5 | DN100x200 mmL GS pipe piece with bore for mounting an air valve. | Nr | 1
5.6.6.6 | DN100x1500 mmL GS pipe piece. | Nr | 1
5.6.6.7 | DN100x250 mmL GS pipe piece, flanged on one side and plain at the opposite end. | Nr | 6
5.6.6.8 | DN100x90o GS slow bend | Nr | 2
5.6.6.9 | DN100 GS socket | Nr | 3
5.6.6.10 | DN100 double flanged GS equal Tee | Nr | 1
5.6.6.11 | DN100 steel Johnson coupling c/w rubber rings. | Nr | 4
5.6.6.12 | 100mmWx5 mm thick rubber gasket | m | 2
5.6.6.13 | DN100x1200 mmL GS pipe piece threaded at both ends | Nr | 1
5.6.6.14 | DN100x2500 mmL double flanged GS pipe piece. | Nr | 1
5.6.6.15 | Any other accessories required for the system | LS | 1
5.6.7 | Removal Of Old Items and Trenching
5.6.7.1 | Excavate, expose and remove existing cables ( power control room to borehole). Trim the trenching to size 450 mmWx500 mm depth. Back fill to ground level after laying of cable. Cart away, dispose excess as advised. | m | 25
5.6.6.2 | Break existing RC pipe support block. | Nr | 1
5.6.6.3 | Excavate to expose and remove a section of existing DN 100 GS Borehole-Rising main inter-connection pipe work. Trim the trenching to size 500 mmW900 mm depth. Back fill to ground level after laying of cable. Cart away , dispose excess as advised. | m | 3
TOTAL PAGE 5
TOTAL BH 1::- CARRIED TO BILLL 5 SUMMARY SHEET

## 5.7_BH2
PART 5.7 - Electro-Mechanical Works & Pipeworks Borehole 2 (Site-Repairs)
ITEM | DESCRIPTION | UNIT | QTY | Rate(KES) | Amount(KES)
5.7.1 | Electro-Mechanical Works
Items below are given for assumed pump capacity, final specifications (e.g. cable thickness) and quantity are dependent on type of pump and pumping depths and have to be identified by the contractor after test pumping
5.7.1.1 | Remove pump set and 60 metres of DN100 GI drop pipes. | LS | 1
SUPPLY, DELIVER TO SITE, INSTALL AND TEST:
NOTE:
5.7.1.2 | Submersible pump set of capacity 48 m3/hr. of water against a total head of 134 metres directly coupled to 3 phase, 415 vac motor, with pump suction inlet at 60 metres below ground level. | Nr | 1
5.7.1.3 | Overheads and profits on item 5.7.1.2 as specified for Prime Cost sum items | %
5.7.1.4 | 16 mm2/4 core submersible pump flat cable | m | 65
5.7.1.5 | DN6x120 mmL stainless steel water level control electrodes. | Pair | 1
5.7.1.6 | OD25 class D uPVC dipper pipe | m | 59
5.7.1.7 | DN100 GI class C threaded water pipe. | m | 60
5.7.1.8 | DN100 GI steam sockets | Nr | 14
5.7.1.9 | DN75x300 mm long GI starter pipe | Nr | 1
5.7.1.10 | DN100x75 GI reducer (female threaded) | Nr | 1
5.7.1.11 | 0.75mm2 sc double insulated copper cable( brown and black) each 65 metres | m | 130
5.7.1.12 | Lay in trench/duct, connect and test 1.5 mm2/2c pvc swa pvc copper cable | m | 20
5.7.1.13 | Lay in trench/duct, connect and test 25 mm2/4c armoured copper cable | m | 20
5.7.1.14 | Copper cable gland c/w lock-nut and shroud for 25 mm2/4 core pvc swa pvc copper cable. | Nr | 2
5.7.1.15 | Copper cable gland c/w lock-nut and shroud for 1.5 mm2/2 core pvc swa pvc copper cable. | Nr | 2
5.7.1.16 | 30 Kw, 3 phase, 415 vac, soft starter panel including integral 3 phase surge arrestor unit. | SET | 1
5.7.1.17 | Masory earth rod chamber of internal size 250x250 x300 mmH extending 50 mm above the ground. It shall be constructed from 150x150x450 mmL masonry blocks (1:3:6). It shall be c/w 75 mm thick perforated cover (1:2:4). | Nr | 1
5.7.1.18 | D15x2.4 metre copper earth rod c/w clamp in a masonry chamber. | Nr | 1
5.7.1.19 | 35 mm2 sc copper cable (green) | m | 5
5.7.1.20 | Supply and install water-tight GS cable junction box of size 125x125x90mm depth, fabricated from 3 mm thick plate.. It shall have GS DIN plate fixed at the inside centre but raised by 10 mm from back side,. 3 No. 10 amps and 5 No. 60 amps cable terminal blocks mounted on the plate, tough rubber cable grommets for 16mm2/4c and 0.75 mm2 sc submerssible cables. | Nr | 1
5.7.1.21 | DN38x150 mmL GI threaded pipe piece (cable entry) | Nr | 1
TOTAL PAGE 1
5.7.1.22 | Supply and installation of Well Probe Sensor complete with well probe cable of size 0.75 mm² of 70 m (to be determined after test pumping). | SET | 1
5.7.1.23 | Supply, installation, testing and commissioning of Electro Magnetic Flow Meter, DN 80, Qmax=80m3/hr, Qnom=40m3/hr, QT=8m3/hr and Qmin=1.2m3/hr, 2 battery power supply, IP 68, RS232 and RS 485 outputs. | Nr | 1
5.7.1.24 | Supply, installation, testing and commissioning of Hydrostatic Level Transmitter with integrated Pt 100 temperature sensor 0-700C, range from 1-100 mH2Og, acuracy + 0.175% FS BSL NLHR>4mH2O, +o.25%<4mH2O. | Nr | 1
5.7.1.25 | INSTALLATION SUNDRIES
5.7.1.25a | ID320x7 mm Thick GS Borehole cap with welded DN100 GI pipe piece, welded DN44 GI slow bend for passage of 25mm2/4c cable, water level control electrodes cables and passage of OD25 mm pvc dipper pipe. | Nr | 1
5.7.1.25b | Boss white (200 gm tin) | Pc | 3
5.7.1.25c | 550 mm plastic cable tie | Nr | 50
5.7.1.25d | 20 mm Wx9ML self bonding electrical tape (scotch 23) | Roll | 2
5.7.1.25e | 12 mm Wx12 ML PTFE thread seal tape | Roll | 15
5.7.1.25f | 20 mm high quality electrical pvc tape (Red, Yellow, Blue, Black) | Roll | 4
5.7.1.25g | Stainless steel ferrules for 16 mm2 cable | Nr | 4
5.7.1.25i | 10 amps cable terminal block | Nr | 3
5.7.1.25j | 60 amps cable terminal block | Nr | 4
Mains Power Control Swichgear Panel and Switch gear/Office Building Wiring
5.7.2 | Mains Power Control Switchgear Panel
5.7.2.1 | Gently clean, air blow, the interior and exterior of the switchgear.
Supply, delivery. Install, wire and Test the following items:
5.7.2.2 | 125 amps, 415 vac TP mcbs (Legrand, DPX) | Nr | 2
5.7.2.2 | 63 amps, 415 vac TP mcbs (Legrand, DPX) | Nr | 2
5.7.2.3 | 12 Kvar, 3 phase, 415 vac, 4 step central automatic power capacitor correction bank c/w 100 amps TP supply mccb, contactors, fuses, programmable electronic PF controller relay, 74 µFcapacitors etc. | SET | 1
5.7.2.4 | 3 phase, 415 vac surge divertor c/w protective mcbs on main 250 amps mccb | SET | 1
5.7.2.5 | 1xCooling fan rated 25 watts, 240 vac, 2800 rpm continuously rated installed on the side, 100 mm height from the bottom clw filter and termite-proof, dust-proof stainless steel protection D1.5 mm wire gauze. | Nr | 1
5.7.2.6 | Ventillation hole of size 150x100 mm installed on the top opposite sides, 50 mm below top c/w termite-proof, dust-proof filter and grid. | Nr | 2
5.7.2.7 | 25x3 mm thick copper strip bound along the switchgear panel length (earthing) | m | 3
5.7.3 | Electrical Repairs of Mains Power Control Switchgear Room
5.7.3.1 | Remove the existing socket/lighting wiring, replace the defective sections of conduit | Item | 1
5.7.3.2 | Re-wire the lighting circuits using 1.5 mm2 single copper cables (Red=15 m, Black=10 m , Green =10 m). | m | 35
5.7.3.3 | 32 amps, TPN + E (5-pin), 415 vac, socket outet (smc) c/w isolator, base and screw top lid, wired using 6 mm2 sc copper cables in 32 mm diameter GS conduit. | No | 1
TOTAL PAGE 2
5.7.3.4 | Re-wire the sockets circuits using 2.5 mm2 single copper cables (Red= 4 m, Black=4 m , Green = 4 m) | m | 12
5.7.3.5 | 10 amps, I way 2 gang switch (IVY white, flush) as Mem, Crabtree or similar quality approved make. | Nr | 1
5.7.3.6 | 13 amps, 240 vac, twin switched socket outlet (IVY White, flush) as Mem, Crabtree or similar quality approved make c/w stainless steel screws (ringmain circuit). | Nr | 1
5.7.3.7 | 36 wattsx1200 mmL single fluorescent lighting fitting, energy save, water tight (IP 20), metal body, corrossion resistant, power factor compensated, c/w tube, starter mounted on ceiling but 20 mm off the surface using 20 mm diam. GS coupler) | Nr | 1
5.7.3.8 | 20 wattsx300 mmL LED fluorescent lighting fitting (IP54), energy save, corrossion resistant, power factor compensated. | Nr | 4
5.7.3.9 | Masory earth rod chamber of internal size 250x250 x300 mmH extending 50 mm above the ground. It shall be constructed from 150x150x450 mmL masonry blocks (1:3:6). It shall be c/w 75 mm thick perforated cover (1:2:4). | Nr | 1
5.7.3.10 | D15x2.4 metre copper earth rod c/w clamp in a masonry chamber.. | Nr | 1
5.7.3.11 | 25 mm2 sc copper cable laid trench and connected to earth rod and main switchgear panel earth bond tape. | m | 3
5.7.3.12 | AC/DC POWER SUPPLY
5.7.3.12.01 | Floor stand supported, 240 ac, 2.5 amps/24 vdc, 20 amps continuosly rated converter fully protected (overload/short-circuit/reverse voltage and polarity etc c/w RJ45, RS232, RS485 ports, mcbs protected outputs to supply water meter, borehole water level measurement, rising main pressure measurement, PLC, Radio/Data Trans-Receiver Equipment. | No. | 1
5.7.3.13 | FIRE FIGHTING EQUIPMENT
5.7.3.13.01 | 5 Kg Class ABC Powder steel cylinder fire extinguisher, c/w pressure gauge wall mounting steel bracket , operating instructions and accessories, fully charged. | No. | 1
5.7.4 | MODIFICATION OF EXISTING BOREOLE No. 2 STARTER PANNEL
5.7.4.1 | 3 phase, 415 vac surge divertor c/w protective mcbs on incomer mccb terminals | Nr | 1
5.7.4.2 | Rewire neatly and label the starter panel. | LS | 1
5.7.4.3 | Replace the existing incomer 125 amps, TP mccb make Terasaki with one rated 100 amps, 415vac) | Nr | 1
5.7.5 | Other Electro-Mechanical Works
5.7.5.1 | Improve lightning protection system | LS | 1
5.7.5.2 | Supply, installation, testing and commissioning of pole mounted 3 phase, 75 Kva, 0.433 Kv/11 Kv ONAN transformer for the site. | Nr | 1
5.7.5.3 | Testing and commissioning of the incoming electricity supply and Main Low Voltage Switchboard | LS | 1
5.7.5.4 | Preparation of all design technical and working drawings for the works for approval prior to commencement of installation of works as per the Specifications. | LS | 1
5.7.5.5 | Allow for all the builders works associated with all the electrical works that the contractor considers necessary to complete works | LS | 1
5.7.5.6 | Painting, varnishing and any other works necessary for making good all the disturbed areas as a result of the new electrical installations | LS | 1
5.7.5.7 | Supply, installation, testing and commissioning of Amplified Pressure Transmitter with pressure range of 16 bar, over pressure safety of 50 bar, from SS material, and power supply 10<UCB<30 VDC and signal output 4-20 mA 2-wire system. | Nr | 1
5.7.5.8 | ID8x3 mm Thick GS tube c/w all necessary mounting fittings, bends etc enclosed in DN15 GS pipe for connection on GS rising main and laid in trenching/duct and connection on pressure switch, pressure gauge at the power supply control room. | m | 25
TOTAL PAGE 3
5.7.5.9 | Adjustable Pressure switch in IP54 metal enclosure, with dual scale (Kg/cm2 and Bar), range 0 - 20 Kg/cm2 (0-20 Bar) connected to GS copper tube and fixed firmly on the wall by GS bracket.. It shall have integral 2NO+2NC auxillary contacts rated 10 amps, 240 vac, stainless steel isolation ball valve. | Nr | 1
5.7.5.10 | High quality pressure gauge - (indoor mounting), with dual scale (Kg/cm2 and Bar).Range (0 - 20 Kg/cm2 )/(0 - 20 bar). It shall be c/w all fitting accessories for connecting on ID8x3mm GS tube. It shall be c/w stainless steel isolation ball valve. | Nr | 1
5.7.5.11 | Single orifice cast steel air valve c/w accessories for mounting on DN100 GI pipe | Nr | 1
5.7.5.12 | Supply, installation, testing and commissioning of 24V DC Power Supply Unit, 500VAC Equipped with one input fuse,187 – 264 VAC, 47 to 63 Hz,0°C….+45°C,≥ IP20, | Nr | 1
5.7.5.13 | Supply, installation and testing of Input /Output interface module (I/O), min. 4 analog inputs 0-10V, 0-20mA, 4-20mA programmable, min 2 digital inputs with frequency range 0-16 Hz | Nr | 1
5.7.5.14 | Supply, installation and testing of Class 10 GPRS Modem, Dual-Band E-GSM/GPRS 900/1800 MHz,GPRS multi-slot class 10,1W@900 MHz,1W@ 1800 MHz,Control via AT commands, -200 C to +550C,RS 232 interface,TCP/IP protocol stack for M2M | Nr | 1
5.7.5.15 | Supply and installation of 1.5mm² armoured underground cable for the well probe | m | 25
5.7.6 | Pressure Pipes and Fittings:
Modification of the connection between the new pump, the suction and the discharge pipes and fittings, and for corresponding concrete works.
5.7.6.1 | Disconnection, dismantling and disposal of old pipes, pipe fittings, valves, water meter. | LS | 1
Supply, delivery to Site, Install and Test:
NOTE: i). All Valves, pipes, pipe fittings, water meter shall be new.
ii). Unless otherwise stated, valves, pipes, pipe fittings, water
meter shall be double flanged, drilled and supplied c/w high
tensile strength stainless steel bolts, nuts and washers.
iii). Cutting and adjustment of pipework on site to fit.
5.7.6.2 | DN 100 mm, PN 16 bar non-slam, non-return valve. | Nr | 1
5.7.6.3 | DN 100 mm, PN 16 bar gate valve. | Nr | 1
5.7.6.4 | DN 100 mm, PN 16 bar Y-strainer | Nr | 1
5.7.6.5 | DN100x200 mmL GS pipe piece with bore for mounting an air valve. | Nr | 1
5.7.6.6 | DN100x500 mmL GS pipe piece. | Nr | 2
5.7.6.7 | DN100x250 mmL GS pipe piece, flanged on one side and plain at the opposite end. | Nr | 1
5.7.6.8 | DN100x90o GS slow bend | Nr | 3
5.7.6.9 | DN100 GS socket | Nr | 3
5.7.6.10 | DN100 double flanged GS equal Tee | Nr | 1
5.7.6.11 | DN100 steel Johnson coupling c/w rubber rings. | Nr | 4
5.7.6.12 | 100mmWx5 mm thick rubber gasket | m | 2
5.7.6.13 | DN100x1200 mmL GS pipe piece threaded at both ends | Nr | 1
5.7.6.14 | DN100x600 mmL GS pipe piece. | Nr | 2
5.7.6.15 | Any other accessories required for the system | LS | 1
5.7.7 | Removal Of Old Items and Trenching
5.7.7.1 | Excavate, expose and remove existing cables ( power control room to borehole). Trim the trenching to size 450 mmWx500 mm depth. Back fill to ground level after laying of cable. Cart away, dispose excess as advised. | m | 20
5.7.7.2 | Break existing RC pipe support block. | Nr | 1
5.7.7.3 | Excavate to expose and remove a section of existing DN 100 GS Borehole-Rising main inter-connection pipe work. Trim the trenching to size 500 mmW900 mm depth. Back fill to ground level after laying of cable. Cart away , dispose excess as advised. | m | 3
TOTAL PAGE 4
TOTAL CARRIED TO BILLL 5 SUMMARY SHEET

## 5.8_BH4,7
PART 5.8 - Electro-Mechanical Works & Pipeworks Boreholes 4 & 7 (Site-Repairs)
5.8.1 | BOREHOLE NO. 4
ITEM | ITEM DESCRIPTION | UNIT | QTY | Rate(KES) | Amount(KES)
5.8.1.1 | Electro-Mechanical Works
Items below are given for assumed pump capacity, final specifications (e.g. cable thickness) and quantity are dependent on type of pump and pumping depths and have to be identified by the contractor after test pumping
5.8.1.1.01 | Remove pump set and drop pipes (Grundfos SP46-12, DN100 GS, Pump depth = 54 metres below ground level | LS | 1
SUPPLY, DELIVER TO SITE, INSTALL AND TEST:
NOTE:
5.8.1.1.02 | Submersible pump set of capacity 50 m3/hr. of water against a total head of 150 metres directly coupled to 3 phase, 415 vac motor, with pump suction inlet at 54 metres below ground level. | Nr | 1
5.8.1.1.03 | Overheads and profits on item 5.8.1.1.02 as specified for Prime Cost sum items | %
5.8.1.1.04 | 16 mm2/4 core submersible pump flat cable | m | 58
5.8.1.1.05 | DN6x120 mmL stainless steel water level control electrodes. | Pair | 1
5.8.1.1.06 | OD25 class D uPVC dipper pipe | m | 52
5.8.1.1.07 | DN100 GI class C threaded water pipe. | m | 52
5.8.1.1.08 | DN100 Steel steam sockets | Nr | 14
5.8.1.1.09 | DN75x300 mm long GI starter pipe | Nr | 1
5.8.1.1.10 | DN100x75 GI reducer (female threaded) | Nr | 1
5.8.1.1.11 | 0.75mm2 sc double insulated copper cable( brown and black) each 58 metres | m | 116
5.8.1.1.12 | Lay in trench/duct, connect and test 1.5 mm2/2c pvc swa pvc copper cable (starter panel to borehole) | m | 20
5.8.1.1.13 | Lay in trench/duct, connect and test 16 mm2/4c armoured copper cable | m | 20
5.8.1.1.14 | Copper cable gland c/w lock-nut and shroud for 16 mm2/4 core pvc swa pvc copper cable. | Nr | 2
5.8.1.1.15 | Copper cable gland c/w lock-nut and shroud for 1.5 mm2/2 core pvc swa pvc copper cable. | Nr | 2
5.8.1.1.16 | 30 Kw, 3 phase, 415 vac, soft starter panel including integral 3 phase surge arrestor unit. | SET | 1
5.8.1.1.17 | Masory earth rod chamber of internal size 250x250 x300 mmH extending 50 mm above the ground. It shall be constructed from 150x150x450 mmL masonry blocks (1:3:6). It shall be c/w 75 mm thick perforated cover (1:2:4). | Nr | 1
5.8.1.1.18 | D15x2.4 metre copper earth rod c/w clamp in a masonry chamber. | Nr | 1
5.8.1.1.19 | 35 mm2 sc copper cable (green) | m | 5
5.8.1.1.20 | Supply and install water-tight GS cable junction box of size 150x150x90mm depth, fabricated from 3 mm thick plate. It shall have GS DIN plate fixed at the inside centre but raised by 10 mm from back side,. 3 No. 10 amps and 5 No. 80 amps cable terminal blocks mounted on the plate, tough rubber cable grommets for 16mm2/4c and 0.75 mm2 sc submerssible cables. | Nr | 1
5.8.1.1.21 | DN38x150 mmL GI threaded pipe piece (cable entry) | Nr | 1
TOTAL PAGE 1
5.8.1.1.22 | Supply and installation of Well Probe Sensor complete with well probe cable of size 0.75 mm² of 70 m (to be determined after test pumping). | SET | 1
5.8.1.1.23 | Supply, installation, testing and commissioning of Electro Magnetic Flow Meter, DN 80, Qmax=80m3/hr, Qnom=40m3/hr, QT=8m3/hr and Qmin=1.2m3/hr, 2 battery power supply, IP 68, RS232 and RS 485 outputs. | Nr | 1
5.8.1.1.24 | Supply, installation, testing and commissioning of Hydrostatic Level Transmitter with integrated Pt 100 temperature sensor 0-700C, range from 1-100 mH2Og, acuracy + 0.175% FS BSL NLHR>4mH2O, +o.25%<4mH2O. | Nr | 1
5.8.1.1.25 | Installation Sundries
5.8.1.1.25a | ID320x7 mm Thick GS Borehole cap with welded DN100 GI pipe piece, welded DN38 GS slow bend for passage of 16mm2/4c pvc swa pvc cu. cable, water level control electrodes cables and passage of OD25 mm pvc dipper pipe. | Nr | 1
5.8.1.1.25b | Boss white (200 gm tin) | pc | 2
5.8.1.1.25c | 550 mm plastic cable tie | Nr | 35
5.8.1.1.25d | 20 mm Wx9ML self bonding electrical tape (scotch 23) | Roll | 1
5.8.1.1.25e | 12 mm Wx12 ML PTFE thread seal tape | Roll | 15
5.8.1.1.25f | 20 mm high quality electrical pvc tape (Red, Yellow, Blue, Black) | Roll | 4
5.8.1.1.25g | Stainless steel ferrules for 16 mm2 cable | Nr | 4
5.8.1.1.25h | Stainless steel ferrules for 0.75mm2 cable | Nr | 3
5.8.1.1.25i | 10 amps cable terminal block | Nr | 3
5.8.1.1.25j | 80 amps cable terminal block | Nr | 4
5.8.1.1.26 | Other Electro-Mechanical Works - BH 4
5.8.1.1.26a | Preparation of all design technical and working drawings for the works for approval prior to commencement of installation of works as per the Specifications. | LS | 1
5.8.1.1.26b | Allow for all the builders works associated with all the electrical works that the contractor considers necessary to complete works | LS | 1
5.8.1.1.26c | Painting, varnishing and any other works necessary for making good all the disturbed areas as a result of the new electrical installations | LS | 1
5.8.1.1.26d | Supply, installation, testing and commissioning of Amplified Pressure Transmitter with pressure range of 16 bar, over pressure safety of 50 bar, from SS material, and power supply 10<UCB<30 VDC and signal output 4-20 mA 2-wire system. | Nr | 1
5.8.1.1.26e | ID8x3 mm Thick GS tube c/w all necessary mounting fittings, bends etc enclosed in DN15 GS pipe for connection on GS rising main and laid in trenching/duct and connection on pressure switch, pressure gauge at the power supply control room. | m | 20
5.8.1.126f | Adjustable Pressure switch in IP54 metal enclosure, with dual scale (Kg/cm2 and Bar), range 0 - 25 Kg/cm2 (0-25 Bar) connected to GS copper tube and fixed firmly on the wall by GS bracket.. It shall have integral 2NO+2NC auxillary contacts rated 10 amps, 240 vac, stainless steel isolation ball valve. | Nr | 1
5.8.1.1.26g | High quality pressure gauge - (indoor mounting), with dual scale (Kg/cm2 and Bar).Range (0 - 25 Kg/cm2 )/(0 - 25 bar). It shall be c/w all fitting accessories for connecting on ID8x3mm GS tube. It shall be c/w stainless steel isolation ball valve. | Nr | 1
5.8.1.1.26h | Single orifice cast steel air valve c/w accessories for mounting on DN100 GS pipe. | Nr | 1
5.8.1.1.26i | Supply, installation, testing and commissioning of 24V DC Power Supply Unit, 500VAC Equipped with one input fuse,187 – 264 VAC, 47 to 63 Hz,0°C….+45°C,≥ IP20. | Nr | 1
5.8.1.1.256j | Supply, installation and testing of Input /Output interface module (I/O), min. 4 analog inputs 0-10V, 0-20mA, 4-20mA programmable, min 2 digital inputs with frequency range 0-16 Hz | Nr | 1
5.8.1.1.26k | Supply, installation and testing of Class 10 GPRS Modem, Dual-Band E-GSM/GPRS 900/1800 MHz,GPRS multi-slot class 10,1W@900 MHz,1W@ 1800 MHz,Control via AT commands, -200 C to +550C,RS 232 interface,TCP/IP protocol stack for M2M | Nr | 1
5.8.1.1.26l | Supply and installation of 1.5mm² armoured underground cable for the well probe | m | 20
TOTAL PAGE 2
5.8.1.1.27 | Pressure Pipes and Fittings:
Modification of the connection between the new pump, the suction and the discharge pipes and fittings, and for corresponding concrete works.
5.8.1.1.27a | Disconnection, dismantling and disposal of old pipes, pipe fittings, valves, water meter. | LS | 1
Supply, delivery to Site, Install and Test:
5.8.1.1.27b | DN100x90o GS slow bend with a bore for pressure gauge and pressure switch (treaded at one end and flanged at the opposite end. | Nr | 1
5.8.1.1.27c | DN100x200 mmL GS pipe piece with bore for mounting an air valve | Nr | 1
5.8.1.1.27d | DN100x1500 mmL GS pipe piece. | Nr | 1
5.8.1.1.27e | DN100x300 mmL GS pipe piece. | Nr | 1
5.8.1.1.27f | DN100x90o GS slow bend | Nr | 2
5.8.1.1.27g | DN100 steel Johnson coupling c/w rubber rings. | Nr | 4
5.8.1.1.27h | 1000mmWx5 mm thick rubber gasket | m | 2
5.8.1.1.27i | DN100x1200 mmL GS pipe piece. | Nr | 1
5.8.1.1.27j | DN100 GS equal Tee | Nr | 1
5.8.1.1.27k | DN100x600 mmL GS pipe piece. | Nr | 2
5.8.1.1.27l | DN150x100 mm GS reducer. | Nr | 1
5.8.1.1.27m | DN100 CS anti-slam, Non-Return valve . | Nr | 1
5.8.1.1.27n | DN100 GI hex nipple | Nr | 5
5.8.1.1.27o | DN100 steel union | Nr | 1
5.8.1.1.27p | DN100 mm, PN 16 bar Y-strainer | Nr | 1
5.8.1.1.27q | DN100x250 mmL GI pipe piece, threaded at one end and plain at the opposite end. | Nr | 1
5.8.1.1.27r | DN150xPN16 gate valve c/w handwheel. | Nr | 1
5.8.1.1.27s | Steel chequered cover plate of size 300 mmWx100 mmLx10mm thick | Nr | 3
5.8.1.1.27t | Any other accessories required for the system | LS | 1
5.8.1.2 | Removal Of Old Items And Trenching
5.8.1.2.01 | Excavate, expose and remove existing cables ( power control room to borehole). Trim the trenching to size 450 mmWx500 mm depth. Back fill to ground level after laying of cable. Cart away , dispose excess as advised. | m | 15
5.8.1.2.02 | Break existing RC pipe support block. | Nr | 1
5.8.1.2.03 | Excavate, expose and remove a section of existing DN 100 GI Borehole-rising main inter-connection pipe work . | m | 3
5.8.1.2.04 | Excavate pipe trench of size 500 mmWx900 mm Depth incompacted soil. Back fill to ground level after laying of the pipe. Cart away , dispose excess as advised. | m | 5
5.8.1.2.05 | Excavate cable trench of size 300 mmWx175 mm Depth floor slab (1:3:6) in the power control room (control power panel to starters and exit holes to boreholes. Straighten the sides and floor. Plaster the sides,place 25 mm thick screed (1:3). Apply nilo on all the surfaces after laying of the pipe. Cart away , dispose debris as advised. | m | 3
TOTAL PAGE 3
5.8.2 BOREHOLE NO. 7
ITEM | ITEM DESCRIPTION | UNIT | QTY | Rate(KES) | Amount(KES)
5.8.2.1 | Electro-Mechanical Works
Items below are given for assumed pump capacity, final specifications (e.g. cable thickness) and quantity are dependent on type of pump and pumping depths and have to be identified by the contractor after test pumping
5.8.2.1.01 | Remove pump set and drop pipes (Grundfos SP46-12, DN100 GS, Pump depth = 54 metres below ground level | LS | 1
SUPPLY, DELIVER TO SITE, INSTALL AND TEST:
NOTE:
5.8.2.1.02 | Submersible pump set of capacity 50 m3/hr. of water against a total head of 150 metres directly coupled to 3 phase, 415 vac motor, with pump suction inlet at 54 metres below ground level. | Nr | 1
5.8.2.1.03 | Overheads and profits on item 5.8.2.1.02 as specified for Prime Cost sum items | %
5.8.2.1.04 | 16 mm2/4 core submersible pump flat cable | m | 58
5.8.2.1.05 | DN6x120 mmL stainless steel water level control electrodes. | Pair | 1
5.8.2.1.06 | OD25 class D uPVC dipper pipe | m | 52
5.8.2.1.07 | DN100 GI class C threaded water pipe. | m | 52
5.8.2.1.08 | DN100 Steel steam sockets | Nr | 14
5.8.2.1.09 | DN75x300 mm long GI starter pipe | Nr | 1
5.8.2.1.10 | DN100x75 GI reducer (female threaded) | Nr | 1
5.8.2.1.11 | 0.75mm2 sc double insulated copper cable( brown and black) each 58 metres | m | 116
5.8.2.1.12 | Lay in trench/duct, connect and test 1.5 mm2/2c pvc swa pvc copper cable (starter panel to borehole) | m | 70
5.8.2.1.13 | Lay in trench/duct, connect and test 25 mm2/4c armoured copper cable | m | 70
5.8.2.1.14 | Copper cable gland c/w lock-nut and shroud for 25 mm2/4 core pvc swa pvc copper cable. | Nr | 2
5.8.2.1.15 | Copper cable gland c/w lock-nut and shroud for 1.5 mm2/2 core pvc swa pvc copper cable. | Nr | 2
5.8.2.1.16 | 30 Kw, 3 phase, 415 vac, soft starter panel including integral 3 phase surge arrestor unit. | SET | 1
5.8.2.1.17 | Masory earth rod chamber of internal size 250x250 x300 mmH extending 50 mm above the ground. It shall be constructed from 150x150x450 mmL masonry blocks (1:3:6). It shall be c/w 75 mm thick perforated cover (1:2:4). | Nr | 1
5.8.2.1.18 | D15x2.4 metre copper earth rod c/w clamp in a masonry chamber. | Nr | 1
5.8.2.1.19 | 35 mm2 sc copper cable (green) | m | 2
5.8.2.1.20 | Supply and install water-tight GS cable junction box of size 175x175x90mm depth, fabricated from 3 mm thick plate. It shall have GS DIN plate fixed at the inside centre but raised by 10 mm from back side,. 3 No. 10 amps and 5 No. 80 amps cable terminal blocks mounted on the plate, tough rubber cable grommets for 25 mm2/4c, 16mm2/4c and 0.75 mm2 sc submerssible cables. | Nr | 1
5.8.2.1.21 | DN38x150 mmL GI threaded pipe piece (cable entry) | Nr | 1
TOTAL PAGE 4
5.8.2.1.22 | Supply and installation of Well Probe Sensor complete with well probe cable of size 0.75 mm² of 70 m (to be determined after test pumping). | SET | 1
5.8.2.1.23 | Supply, installation, testing and commissioning of Electro Magnetic Flow Meter, DN 80, Qmax=80m3/hr, Qnom=40m3/hr, QT=8m3/hr and Qmin=1.2m3/hr, 2 battery power supply, IP 68, RS232 and RS 485 outputs. | No | 1
5.8.2.1.24 | Supply, installation, testing and commissioning of Hydrostatic Level Transmitter with integrated Pt 100 temperature sensor 0-700C, range from 1-100 mH2Og, acuracy + 0.175% FS BSL NLHR>4mH2O, +o.25%<4mH2O. | No | 1
5.8.2.1.25 | Installation Sundries
5.8.2.1.25a | ID320x7 mm Thick GS Borehole cap with welded DN100 GI pipe piece, welded DN38 GS slow bend for passage of 16mm2/4c pvc swa pvc cu. cable, water level control electrodes cables and passage of OD25 mm pvc dipper pipe. | Nr | 1
5.8.2.1.25b | Boss white (200 gm tin) | pc | 2
5.8.2.1.25c | 550 mm plastic cable tie | Nr | 35
5.8.2.1.25d | 20 mm Wx9ML self bonding electrical tape (scotch 23) | Roll | 2
5.8.2.1.25e | 12 mm Wx12 ML PTFE thread seal tape | Roll | 15
5.8.2.1.25f | 20 mm high quality electrical pvc tape (Red, Yellow, Blue, Black) | Roll | 4
5.8.2.1.25g | Stainless steel ferrules for 16 mm2 cable | Nr | 4
5.8.2.1.25h | Stainless steel ferrules for 0.75 mm2 cable | Nr | 3
5.8.2.1.25i | 10 amps cable terminal block | Nr | 3
5.8.2.1.25j | 80 amps cable terminal block | Nr | 4
5.8.2.1.26 | Other Electro-Mechanical Works - BH 7
5.8.2.1.26a | Preparation of all design technical and working drawings for the works for approval prior to commencement of installation of works as per the Specifications. | LS | 1
5.8.2.1.26b | Allow for all the builders works associated with all the electrical works that the contractor considers necessary to complete works | LS | 1
5.8.2.1.26c | Painting, varnishing and any other works necessary for making good all the disturbed areas as a result of the new electrical installations | LS | 1
5.8.2.1.26d | Supply, installation, testing and commissioning of Amplified Pressure Transmitter with pressure range of 16 bar, over pressure safety of 50 bar, from SS material, and power supply 10<UCB<30 VDC and signal output 4-20 mA 2-wire system. | Nr | 1
5.8.2.1.26e | ID8x3 mm Thick GS tube c/w all necessary mounting fittings, bends etc enclosed in DN15 GS pipe for connection on GS rising main and laid in trenching/duct and connection on pressure switch, pressure gauge at the power supply control room. | m | 70
5.8.2.1.26f | Adjustable Pressure switch in IP54 metal enclosure, with dual scale (Kg/cm2 and Bar), range 0 - 25 Kg/cm2 (0-25 Bar) connected to GS copper tube and fixed firmly on the wall by GS bracket.. It shall have integral 2NO+2NC auxillary contacts rated 10 amps, 240 vac, stainless steel isolation ball valve. | Nr | 1
5.8.2.1.26g | High quality pressure gauge - (indoor mounting), with dual scale (Kg/cm2 and Bar).Range (0 - 25 Kg/cm2 )/(0 - 25 bar). It shall be c/w all fitting accessories for connecting on ID8x3mm GS tube. It shall be c/w stainless steel isolation ball valve. | Nr | 1
5.8.2.1.26h | Single orifice cast steel air valve c/w accessories for mounting on DN100 GS pipe. | Nr | 1
5.8.2.1.26i | Supply, installation, testing and commissioning of 24V DC Power Supply Unit, 500VAC Equipped with one input fuse,187 – 264 VAC, 47 to 63 Hz,0°C….+45°C,≥ IP20. | Nr | 1
5.8.2.1.26j | Supply, installation and testing of Input /Output interface module (I/O), min. 4 analog inputs 0-10V, 0-20mA, 4-20mA programmable, min 2 digital inputs with frequency range 0-16 Hz | Nr | 1
5.8.2.1.26k | Supply, installation and testing of Class 10 GPRS Modem, Dual-Band E-GSM/GPRS 900/1800 MHz,GPRS multi-slot class 10,1W@900 MHz,1W@ 1800 MHz,Control via AT commands, -200 C to +550C,RS 232 interface,TCP/IP protocol stack for M2M | Nr | 1
5.8.2.1.26l | Supply and installation of 1.5mm² armoured underground cable for the well probe | LM | 70
TOTAL PAGE 5
5.8.2.1.27 | Pressure Pipes and Fittings:
Modification of the connection between the new pump, the suction and the discharge pipes and fittings, and for corresponding concrete works.
5.8.2.1.27a | Disconnection, dismantling and disposal of old pipes, pipe fittings, valves, water meter. | LS | 1
Supply, delivery to Site, Install and Test:
NOTE: i). All Valves, pipes, pipe fittings, water meter shall be new.
ii). Unless otherwise stated, valves, pipes, pipe fittings, water
meter shall be double flanged, drilled and supplied c/w high
tensile strength stainless steel bolts, nuts and washers.
iii). Cutting and adjustment of pipework on site to fit.
5.8.2.1.27b | DN100x90o GS slow bend with a bore for pressure gauge and pressure switch (treaded at one end and flanged at the opposite end. | Nr | 1
5.8.2.1.27c | DN100x200 mmL GS pipe piece with bore for mounting an air valve | Nr | 1
5.8.2.1.27d | DN100x1500 mmL GS pipe piece. | Nr | 1
5.8.2.1.27e | DN100x300 mmL GS pipe piece. | Nr | 3
5.8.2.1.27f | DN100x90o GS slow bend | Nr | 2
5.8.2.1.27g | DN100 steel Johnson coupling c/w rubber rings. | Nr | 4
5.8.2.1.27h | 1000mmWx5 mm thick rubber gasket | m | 2
5.8.2.1.27i | DN100x1500 mmL GS pipe piece. | Nr | 1
5.8.2.1.27j | DN100 GS equal Tee | Nr | 1
5.8.2.1.27k | DN100x600 mmL GS pipe piece. | Nr | 2
5.8.2.1.27l | DN100 CS anti-slam, Non-Return valve . | Nr | 1
5.8.2.1.27m | DN100 GI hex nipple | Nr | 8
5.8.2.1.27n | DN100 steel union | Nr | 1
5.8.2.1.27o | DN100 mm, PN 16 bar Y-strainer | Nr | 1
5.8.2.1.27p | DN100x250 mmL GI pipe piece, threaded at one end and plain at the opposite end. | Nr | 1
5.8.2.1.27q | DN100xPN16 gate valve c/w handwheel. | Nr | 1
5.8.2.1.27r | DN150x100 GI reducer. | Nr | 1
5.8.2.1.27s | DN150 CS Non-Return valve. | Nr | 1
5.8.2.1.27t | Any other accessories required for the system | LS | 1
5.8.2.2 | Removal Of Old Items and Trenching
5.8.2.2.01 | Excavate, expose and remove existing cables ( power control room to borehole). Trim the trenching to size 450 mmWx500 mm depth. Back fill to ground level after laying of cable. Cart away , dispose excess as advised. | m | 65
5.8.2.2.02 | Excavate, expose and remove a section of existing DN 100 GI Borehole-rising main inter-connection pipe work . | m | 4
5.8.2.2.03 | Excavate pipe trench of size 500 mmWx900 mm Depth in compacted soil. Back fill to ground level after laying of the pipe. Cart away, dispose excess as advised. | m | 5
TOTAL PAGE 6
5.8.3. NEW MAINS POWER CONTROL SWITCHGEAR PANEL, ELECTRICAL
AND FIRE FIGHTING EQUIPMENT
5.8.3.1 | NEW MAINS POWER CONTROL SWITCHGEAR PANEL
5.8.3.1.01 | Free standing, 250 amps, 3 phase, 415 vac, compact, compartmented, indoor, surface metal clad maiins power control panel (IP20), dust-proof, termite-proof, comprising of but not limited to the following, duly wired and labeled. It shall be constructed from gauge 16 spangled sheet steel of minimum thickness 1.75mm; | Nr | 1
5.8.3.1.02 | Kenya Power & Lighting Company CUT-OUTS chamber | Nr | 1
5.8.3.1.03 | 1xKPLC incommer Current transformers chamber | Nr | 1
5.8.3.1.04 | 1xKPLC metering equipment chamber incommer Current transformers chamber | Nr | 1
5.8.3.1.05 | 1x250 amps adjustable triple pole mccb (adjustable range: 0.7IN, 0.8IN, 0.9IN, 1.0IN set at 0.8IN where IN= rated current of mccb = 250 amps). | Nr | 1
5.8.3.1.06 | 1x25 Kvar, 3 phase, 415 vac, 5 step central automatic power capacitor correction bank c/w 100 amps TP supply mccb, contactors, fuses, programmable electronic PF controllerrelay etc. | Nr | 1
5.8.3.1.07 | 1xsingle phase, 240 vac kWh energy registering meter) | Nr | 1
5.8.3.1.08 | 4x260 amps high conductivity rectangular bare copper bus-bar conductors | Nr | 1
5.8.3.1.09 | 2x125 amps, TP, 415 vac, mccbs, ICU =25 kA. Each in its own cmpartment (1 No. for Borehole No.4, 1 No. for BH No.7, and 2 No. spares. | Nr | 1
5.8.3.1.10 | 2x63 amps, TP, 415 vac, mccbs, ICU =15 kA. Each in its own cmpartment. (Spares) | Nr | 1
5.8.3.1.11 | 1x3 phase, 415 vac surge divertor c/w protective mcbs on main 250 amps mccb | Nr | 1
5.8.3.1.12 | 2x100 amps,1phase, 240 vac class "A" mcbs (staff houses) | Nr | 1
5.8.3.1.13 | 1xCooling fan rated 25 watts, 240 vac, 2800 rpm continuously rated installed on the side, 100 mm height from the bottom clw filter and termite-proof, dust-proof stainless steel protection D1.5 mm wiregauze. | Nr | 1
5.8.3.1.14 | 2x ventillation hole of size 150x100 mm installed on the top opposite sides, 50 mm below top c/w termite-proof, dust-proof filter and grid. | Nr | 1
5.8.3.1.15 | 1x3 phase, 240 vac resettable digital network analyzer/recorder (voltage, current, kWh, Kva, Pf,Hz, Kw) with LED phase indicators (RED, YELLOW, BLUE) on front panel. | Nr | 1
5.8.3.1.16 | 100 amps, 6 way, 1 phase, 240 vac DIN distribution board; c/w; 2 No. 10 amps,1 pole, 240 vac class "A" mcbs, 3 No. 20 amps, 1 pole class "A" mcbs, 1 No. Blanking plate. | Nr | 1
5.8.3.1.17 | 3xAC ammeters range 0-300 amps c/w CTS. | Nr | 1
5.8.3.1.18 | 1xAC voltmeter (0-500 vac) c/w vss and protection mcbs. | Nr | 1
5.8.3.1.19 | 32 amps, TPN + E (5-pin), 415 vac, socket outet (smc) c/w isolator, base and screw top lid. | Nr | 1
5.8.3.1.20 | 250 amps, 415 vac TPN manual changer-over switch c/w pilot indicator lights ( KPLC ON, KPLC LOAD ON, GENERATOR ON, GENERATOR LOAD ON) | Nr | 1
5.8.3.1.21 | 25x3 mm thick copper strip bound along the switchgear panel length (earthing) | SET | 1
5.8.3.2 | Electrical Repairs of Mains Power Control Switchgear/Office/Chemical Dosing Room
5.8.2.1 | Remove the existing socket/lighting wiring. | LS | 1
5.8.2.2 | 20 mm diam. GS conduit fixed on the walls and roof members. The cost shall be inclusive of tees, bends, circular boxes with covers, other necessary accessories | m | 108
5.8.2.3 | 1.5 mm2 single copper cables (Red=150 m, Black=120 m , Green =120 m) laid in GS conduit and terminated at boh ends. | m | 390
TOTAL PAGE 7
5.8.2.4 | 2.5 mm2 single copper cables (Red=80 m, Black=80 m , Green =80 m) laid in GS conduit and terminated at both ends. | m | 240
5.8.2.5 | 10 amps, I way 2 gang switch (smc) as Mem, Crabtree or similar quality approved make c/w box and ss screws | Nr | 1
| 10 amps, I way 1 gang switch (smc) as Mem, Crabtree or similar quality approved make c/w box and ss screws | Nr | 2
5.8.2.6 | 13 amps, 240 vac, twin switched socket outlet (smc) as Mem, Crabtree or similar quality approved make c/w box stainless steel screws (ringmain circuit). | Nr | 6
5.8.2.7 | 36 wattsx1200 mmL single fluorescent lighting fitting, energy save, water tight (IP 20), metal body, corrossion resistant, power factor compensated, c/w tube, starter mounted on ceiling but 20 mm off the surface using 20 mm diam. GS coupler) | Nr | 4
5.8.2.8 | 20 wattsx300 mmL LED fluorescent lighting fitting (IP54), energy save, corrossion resistant, power factor compensated. | Nr | 6
5.8.2.9 | Masory earth rod chamber of internal size 250x250 x300 mmH extending 50 mm above the ground. It shall be constructed from 150x150x450 mmL masonry blocks (1:3:6). It shall be c/w 75 mm thick perforated cover (1:2:4). | Nr | 1
5.8.2.10 | D15x2.4 metre copper earth rod c/w clamp in a masonry chamber.. | Nr | 1
5.8.2.11 | 35 mm2 sc copper cable laid trench and connected to earth rod and main switchgear panel earth bond tape. | m | 5
5.8.2.12 | Improve lightning protection system | LS | 1
5.8.3. | AC/DC POWER SUPPLY
5.8.3.01 | Floor stand supported, 240 ac, 2.5 amps/24 vdc, 20 amps continuosly rated converter fully protected (overload/short-circuit/reverse voltage and polarity etc c/w RJ45, RS232, RS485 ports, mcbs protected outputs to supply water meter, borehole water level measurement, rising main pressure measurement, PLC, Radio/Data Trans-Receiver Equipment. | SET | 1
5.8.4 | Fire Fighting Equipment
5.8.4.1 | 5 Kg Class ABC Powder steel cylinder fire extinguisher, c/w pressure gauge wall mounting steel bracket , operating instructions and accessories, fully charged. | No | 2
TOTAL PAGE 8
TOTAL BHs 4 & 7:- CARRIED TO BILLL 5 SUMMARY SHEET

## 5.9_BH6.1,6.2
PART 5.9 - Electro-Mechanical Works & Pipeworks Boreholes 6.1 & 6.2 (Site-Repairs)
5.9.1 | BOREHOLE NO. 6.1
ITEM | ITEM DESCRIPTION | UNIT | QTY | Rate(KES) | Amount(KES)
5.9.1.1 | Electro-Mechanical Works
Items below are given for assumed pump capacity, final specifications (e.g. cable thickness) and quantity are dependent on type of pump and pumping depths and have to be identified by the contractor after test pumping
SUPPLY, DELIVER TO SITE, INSTALL AND TEST:
NOTE:
5.9.1.1.01 | Submersible pump set of capacity 22.5 m3/hr. of water against a total head of 175 metres directly coupled to 3 phase, 415 vac motor, with pump suction inlet at 55 metres below ground level c/w cable guard. | Nr | 1
5.9.1.1.02 | Overheads and profits on item 5.9.1.1.02 as specified for Prime Cost sum items | %
5.9.1.1.03 | 10 mm2/4 core submersible pump flat cable | m | 58
5.9.1.1.05 | DN6x120 mmL stainless steel water level control electrodes. | Pair | 1
5.9.1.1.06 | OD25 class D uPVC dipper pipe | m | 55
5.9.1.1.07 | DN100 GS class C threaded water pipe. | m | 54
5.9.1.1.08 | DN100 Steel steam sockets | Nr | 12
5.9.1.1.09 | DN75x300 mm long GS starter pipe | Nr | 1
5.9.1.1.10 | DN100x75 GS reducer (female threaded) | Nr | 1
5.9.1.1.11 | 0.75mm2 sc double insulated copper cable( brown and black) each 58 metres | m | 116
5.9.1.1.12 | Lay in trench/duct, connect and test 1.5 mm2/2c pvc swa pvc copper cable (starter panel to borehole) | m | 30
5.9.1.1.13 | Lay in trench/duct, connect and test 16 mm2/4c armoured copper cable | m | 30
5.9.1.1.14 | Copper cable gland c/w lock-nut and shroud for 16 mm2/4 core pvc swa pvc copper cable. | Nr | 2
5.9.1.1.15 | Copper cable gland c/w lock-nut and shroud for 1.5 mm2/2 core pvc swa pvc copper cable. | Nr | 2
5.9.1.1.16 | 18.5 Kw, 3 phase, 415 vac, soft starter panel including integral 3 phase surge arrestor unit. | SET | 1
5.9.1.1.17 | Masory earth rod chamber of internal size 250x250 x300 mmH extending 50 mm above the ground. It shall be constructed from 150x150x450 mmL masonry blocks (1:3:6). It shall be c/w 75 mm thick perforated cover (1:2:4). | Nr | 1
5.9.1.1.18 | D15x2.4 metre copper earth rod c/w clamp in a masonry chamber. | Nr | 1
5.9.1.1.19a | Supply and install water-tight GS cable junction box of size 150x150x90mm depth, fabricated from 3 mm thick plate.. It shall have GS DIN plate fixed at the inside centre but raised by 10 mm from back side. 3 No. 10 amps and 5 No. 60 amps cable terminal blocks mounted on the plate, tough rubber cable grommets for 16mm2/4c and 0.75 mm2 sc submerssible cable. | Nr | 1
5.9.1.1.19b | 35 mm2 sc copper cable (green) | m | 5
5.9.1.1.20 | DN38x150 mmL GS threaded pipe piece (cable entry) | Nr | 1
5.9.1.1.21 | Supply and installation of Well Probe Sensor complete with well probe cable of size 0.75 mm² of 70 m (to be determined after test pumping). | SET | 1
5.9.1.1.22 | Supply, installation, testing and commissioning of Electro Magnetic Flow Meter, DN80, Qmax=80m3/hr, Qnom=40m3/hr, QT=8m3/hr and Qmin=1.2m3/hr, 2 battery power supply, IP 68, RS232 and RS 485 outputs. | Nr | 1
TOTAL PAGE 1
5.9.1.1.23 | Supply, installation, testing and commissioning of Hydrostatic Level Transmitter with integrated Pt 100 temperature sensor 0-700C, range from 1-100 mH2Og, acuracy + 0.175% FS BSL NLHR>4mH2O, +o.25%<4mH2O. | Nr | 1
5.9.1.1.24 | Installation Sundries
5.9.1.1.24a | ID220x4 mm Thick GS Borehole cap with welded DN75 GS pipe piece, welded DN38 GS slow bend for passage of 16mm2/4c cable, water level control electrodes cables and passage of OD25 mm pvc dipper pipe. | Nr | 1
5.9.1.1.24b | Boss white (200 gm tin) | pc | 2
5.9.1.1.24c | 550 mm plastic cable tie | Nr | 40
5.9.1.1.24d | 20 mm Wx9ML self bonding electrical tape (scotch 23) | ROLL | 2
5.9.1.1.24e | 12 mm Wx12 ML PTFE thread seal tape | ROLL | 10
5.9.1.1.24f | 20 mm high quality electrical pvc tape (Red, Yellow, Blue, Black) | ROLL | 4
5.9.1.1.24g | Stainless steel ferrules for 10mm2 cable | Nr | 4
5.9.1.1.24h | Stainless steel ferrules for 0.75 mm2 cable | Nr | 2
5.9.1.1.24i | 10 amps cable terminal block | Nr | 3
5.9.1.1.24j | 60 amps cable terminal block | Nr | 4
5.9.1.1.25 | Other Electro-mechanical Works - BH 6.1
5.9.1.1.25a | Preparation of all design technical and working drawings for the works for approval prior to commencement of installation of works as per the Specifications. | LS | 1
5.9.1.1.25b | Allow for all the builders works associated with all the electrical works that the contractor considers necessary to complete works | LS | 1
5.9.1.1.25c | Painting, varnishing and any other works necessary for making good all the disturbed areas as a result of the new electrical installations. | LS | 1
5.9.1.1.25d | Supply, installation, testing and commissioning of Amplified Pressure Transmitter with pressure range of 20 bar, over pressure safety of 50 bar, from SS material, and power supply 10<UCB<30 VDC and signal output 4-20 mA 2-wire system. | Nr | 1
5.9.1.1.25e | ID8x3 mm Thick GS tube c/w all necessary mounting fittings, bends etc enclosed in DN15 GS pipe for connection on GS rising main and laid in trenching/duct and connection on pressure switch, pressure gauge at the power supply control room. | m | 30
5.9.1.1.25f | Adjustable Pressure switch in IP54 metal enclosure, with dual scale (Kg/cm2 and Bar), range 0 - 25 Kg/cm2 (0 - 25 Bar) connected to GS copper tube and fixed firmly on the wall by GS bracket. It shall have integral 2NO+2NC auxillary contacts rated 10 amps, 240 vac, stainless steel isolation ball valve. | nr | 1
5.9.1.1.25g | High quality pressure gauge - (indoor mounting), with dual scale (Kg/cm2 and Bar).Range (0 - 30 Kg/cm2 )/(0 - 30 bar). It shall be c/w all fitting accessories for connecting on ID8x3mm GS tube. It shall be c/w stainless steel isolation ball valve. | Nr | 1
5.9.1.1.25h | Single orifice cast steel air valve c/w accessories for mounting on DN75 GS pipe. | Nr | 1
5..1.1.25i | Supply, installation, testing and commissioning of 24V DC Power Supply Unit, 500VAC Equipped with one input fuse, 187 – 264 VAC, 47 to 63 Hz,0°C….+45°C,≥ IP20. | Nr | 1
TOTAL PAGE 2
5.9.1.1.25j | Supply, installation and testing of Input /Output interface module (I/O), min. 4 analog inputs 0-10V, 0-20mA, 4-20mA programmable, min 2 digital inputs with frequency range 0-16 Hz. | Nr | 1
5.9.1.1.25k | Supply, installation and testing of Class 10 GPRS Modem, Dual-Band E-GSM/GPRS 900/1800 MHz,GPRS multi-slot class 10,1W@900 MHz,1W@ 1800 MHz,Control via AT commands, -200 C to +550C,RS 232 interface,TCP/IP protocol stack for M2M | Nr | 1
5.9.1.1.25l | Supply and installation of 1.5mm² armoured underground cable for the well probe | m | 30
5.9.1.1.26 | Pressure Pipes and Fittings:
Modification of the connection between the new pump, the suction and the discharge pipes and fittings, and for corresponding concrete works.
5.9.1.1.26a | Disconnection, dismantling and disposal of old pipes, pipe fittings, valves, water meter. | LS | 1
Supply, delivery to Site, Install and Test:
NOTE: i). All Valves, pipes, pipe fittings, water meter shall be new.
ii). Unless otherwise stated, valves, pipes, pipe fittings, water
meter shall be double flanged, drilled and supplied c/w high
tensile strength stainless steel bolts, nuts and washers.
iii). Cutting and adjustment of pipework on site to fit.
5.9.1.1.26b | DN100x90o GS slow bend with a bore for pressure gauge | Nr | 3
5.9.1.1.26c | DN100 GS socket with bore for mounting air valve | Nr | 1
5.9.1.1.26d | DN100x75 GS reducer. | Nr | 1
5.9.1.1.26e | DN100x1500 mmL GS pipe piece | Nr | 1
5.9.1.1.26f | DN100x300 mmL GS pipe piece. | Nr | 2
5.9.1.1.26g | DN100x90o GS slow bend | Nr | 2
5.9.1.1.26h | DN100 CS non-slam, Non-Return valve. | Nr | 1
5.9.1.1.26i | DN100 steel Johnson coupling c/w rubber rings. | Nr | 3
5.9.1.1.26k | DN100xPN20 gate valve c/w handwheel. | Nr | 2
5.9.1.1.26l | DN100, PN 20 bar Y-strainer | Nr | 1
5.9.1.2 | Removal Of Old Items And Trenching
5.9.1.2.01 | Excavate, expose and remove existing cables ( power control room to borehole). Trim the trenching to size 450 mmWx500 mm depth. Back fill to ground level after laying of cable. Cart away, dispose excess as advised. | m | 20
5.9.1.2.02 | Excavate, expose and remove a section of existing DN100 GS Borehole-rising main inter-connection pipe work. Trim the trenching to size 500 mmWx600 mm depth. Back fill to ground level after laying of pipe. Cart away, dispose excess as advised. | m | 5
TOTAL PAGE 3
5.9.2 | BOREHOLE NO. 6.2
ITEM | ITEM DESCRIPTION | UNIT | QTY | Rate(KES) | Amount(KES)
5.9.2.1 | Electro-Mechanical Works
Items below are given for assumed pump capacity, final specifications (e.g. cable thickness) and quantity are dependent on type of pump and pumping depths and have to be identified by the contractor after test pumping
5.9.2.1.01 | Remove pump set and drop pipes (Grundfos SP17-17, DN75 GS, Pump inlet depth = 73 metres below ground level | LS | 1
SUPPLY, DELIVER TO SITE, INSTALL AND TEST:
NOTE:
5.9.2.1.02 | Submersible pump set of capacity 11 m3/hr. of water against a total head of 175 metres directly coupled to 3 phase, 415 vac motor, with pump suction inlet at 73 metres below ground level. | Nr | 1
5.9.2.1.03 | Overheads and profits on item 5.9.2.1.02 as specified for Prime Cost sum items | %
5.9.2.1.04 | 16 mm2/4 core submersible pump flat cable | m | 75
5.9.2.1.05 | DN6x120 mmL stainless steel water level control electrodes. | Pair | 1
5.9.2.1.06 | OD25 class D uPVC dipper pipe | m | 73
5.9.2.1.07 | DN75 GS class C threaded water pipe. | m | 73
5.9.2.1.08 | DN75 Steel steam sockets | Nr | 15
5.9.2.1.09 | DN65x300 mm long GS starter pipe | Nr | 1
5.9.2.1.10 | DN75x65 GS reducer (female threaded) | Nr | 1
5.9.2.1.11 | 0.75mm2 sc double insulated copper cable( brown and black) each 75 metres | m | 150
5.9.2.1.12 | Lay in trench/duct, connect and test 1.5 mm2/2c pvc swa pvc copper cable (starter panel to borehole) | m | 170
5.9.2.1.13 | Lay in trench/duct, connect and test 16 mm2/4c armoured copper cable | m | 170
5.9.2.1.14 | Copper cable gland c/w lock-nut and shroud for 16 mm2/4 core pvc swa pvc copper cable. | Nr | 2
5.9.2.1.15 | Copper cable gland c/w lock-nut and shroud for 1.5 mm2/2 core pvc swa pvc copper cable. | Nr | 2
5.9.2.1.16 | Masory earth rod chamber of internal size 250x250 x300 mmH extending 50 mm above the ground. It shall be constructed from 150x150x450 mmL masonry blocks (1:3:6). It shall be c/w 75 mm thick perforated cover (1:2:4). | Nr | 1
5.9.2.1.17 | D15x2.4 metre copper earth rod c/w clamp in a masonry chamber. | Nr | 1
5.9.2.1.18 | 16 mm2 sc copper cable (green) | m | 5
5.9.2.1.19 | Supply and install water-tight GS cable junction box of size 150x150x90mm depth, fabricated from 3 mm thick plate.. It shall have GS DIN plate fixed at the inside centre but raised by 10 mm from back side. 3 No. 10 amps and 5 No. 30 amps cable terminal blocks mounted on the plate, tough rubber cable grommets for 16mm2/4c and 0.75 mm2 sc submerssible cable. | Nr | 1
5.9.2.1.20 | DN38x150 mmL GS threaded pipe piece (cable entry) | Nr | 1
5.9.2.1.21 | Supply and installation of Well Probe Sensor complete with well probe cable of size 0.75 mm² of 70 m (to be determined after test pumping). | SET | 1
TOTAL PAGE 4
5.9.2.1.22 | Supply, installation, testing and commissioning of Electro Magnetic Flow Meter, DN80, Qmax=80m3/hr, Qnom=40m3/hr, QT=8m3/hr and Qmin=1.2m3/hr, 2 battery power supply, IP 68, RS232 and RS 485 outputs. | Nr | 1
5.9.2.1.23 | Supply, installation, testing and commissioning of Hydrostatic Level Transmitter with integrated Pt 100 temperature sensor 0-700C, range from 1-100 mH2Og, acuracy + 0.175% FS BSL NLHR>4mH2O, +o.25%<4mH2O. | Nr | 1
5.9.2.1.24 | Installation Sundries
5.9.2.1.24a | ID220x4 mm Thick GS Borehole cap with welded DN75 GS pipe piece, welded DN38 GI slow bend for passage of 16mm2/4c cable, water level control electrodes cables and passage of OD25 mm pvc dipper pipe. | Nr | 1
5.9.2.1.24b | Boss white (200 gm tin) | pc | 2
5.9.2.1.24c | 450 mm plastic cable tie | Nr | 50
5.9.2.1.24d | 20 mm Wx9ML self bonding electrical tape (scotch 23) | ROLL | 2
5.9.2.1.24e | 12 mm Wx12 ML PTFE thread seal tape | ROLL | 10
5.9.2.1.24f | 20 mm high quality electrical pvc tape (Red, Yellow, Blue, Black) | ROLL | 4
5.9.2.1.24g | Stainless steel ferrules for 16mm2 cable | Nr | 4
5.9.2.1.24h | Stainless steel ferrules for 0.75 mm2 cable | Nr | 2
5.9.2.1.24i | 10 amps cable terminal block | Nr | 3
5.9.2.1.24j | 30 amps cable terminal block | Nr | 4
5.9.2.1.25 | Other Electro-mechanical Works - BH 6.2
5.9.2.1.25a | Preparation of all design technical and working drawings for the works for approval prior to commencement of installation of works as per the Specifications. | LS | 1
5.9.2.1.25b | Allow for all the builders works associated with all the electrical works that the contractor considers necessary to complete works. | LS | 1
5.9.2.1.25c | Painting, varnishing and any other works necessary for making good all the disturbed areas as a result of the new electrical installations. | LS | 1
5.9.2.1.25d | Supply, installation, testing and commissioning of Amplified Pressure Transmitter with pressure range of 20 bar, over pressure safety of 50 bar, from SS material, and power supply 10<UCB<30 VDC and signal output 4-20 mA 2-wire system. | Nr | 1
5.9.2.1.25e | ID8x3 mm Thick GS tube c/w all necessary mounting fittings, bends etc enclosed in DN15 GS pipe for connection on GS rising main and laid in trenching/duct and connection on pressure switch, pressure gauge at the power supply control room. | m | 165
5.9.2.1.25f | Adjustable Pressure switch in IP54 metal enclosure, with dual scale (Kg/cm2 and Bar), range 0 - 25 Kg/cm2 (0 - 25 Bar) connected to GS copper tube and fixed firmly on the wall by GS bracket. It shall have integral 2NO+2NC auxillary contacts rated 10 amps, 240 vac, stainless steel isolation ball valve. | nr | 1
Total page 5
5.9.2.1.25g | High quality pressure gauge - (indoor mounting), with dual scale (Kg/cm2 and Bar).Range (0 - 30 Kg/cm2 )/(0 - 30 bar). It shall be c/w all fitting accessories for connecting on ID8x3mm GS tube. It shall be c/w stainless steel isolation ball valve. | Nr | 1
5.9.2.1.25h | Single orifice cast steel air valve c/w accessories for mounting on DN75 GS pipe. | Nr | 1
5..9.2.1.25i | Supply, installation, testing and commissioning of 24V DC Power Supply Unit, 500VAC Equipped with one input fuse, 187 – 264 VAC, 47 to 63 Hz,0°C….+45°C,≥ IP20. | Nr | 1
5.9.2.1.25j | Supply, installation and testing of Input /Output interface module (I/O), min. 4 analog inputs 0-10V, 0-20mA, 4-20mA programmable, min 2 digital inputs with frequency range 0-16 Hz | Nr | 1
5.9.2.1.25k | Supply, installation and testing of Class 10 GPRS Modem, Dual-Band E-GSM/GPRS 900/1800 MHz,GPRS multi-slot class 10,1W@900 MHz,1W@ 1800 MHz,Control via AT commands, -200 C to +550C,RS 232 interface,TCP/IP protocol stack for M2M | Nr | 1
5.9.2.1.25l | Supply and installation of 1.5mm² armoured underground cable for the well probe | m | 170
5.9.2.1.26 | Pressure Pipes and Fittings:
Modification of the connection between the new pump, the suction and the discharge pipes and fittings, and for corresponding concrete works.
5.9.2.1.26a | Disconnection, dismantling and disposal of old pipes, pipe fittings, valves, water meter. | LS | 1
Supply, delivery to Site, Install and Test:
5.9.2.1.26b | DN75x90o GS slow bend with a bore for pressure gauge | Nr | 3
5.9.2.1.26c | DN75 GS socket with bore for mounting air valve | Nr | 1
5.9.2.1.26d | DN75x50 GS reducer (threaded) | Nr | 1
5.9.2.1.26e | DN75x1500 GS pipe piece (threaded at both ends) | Nr | 1
5.9.2.1.26f | DN75x300 GS pipe piece )(threaded at both ends | Nr | 1
5.9.21.26g | DN75x90o GS slow bend | Nr | 2
TOTAL PAGE 6
5.9.2.1.26h | DN75 GS hex nipple | Nr | 4
5.9.2.1.26i | DN75 GS union (threaded) | Nr | 3
5.9.2.1.26j | DN75 stainless steel non-slam, Non-Return valve (threaded) | Nr | 1
5.9.2.1.26k | DN75 steel Johnson coupling c/w rubber rings. | Nr | 2
5.9.2.1.26l | DN75xPN20 gate valve c/w handwheel. | Nr | 2
5.9.2.1.26m | DN75, PN 20 bar Y-strainer | Nr | 1
5.9.2.2 | Removal Of Old Items and Trenching
5.9.2.2.01 | Excavate, expose and remove existing cables ( power control room to borehole). Trim the trenching to size 450 mmWx500 mm depth. Back fill to ground level after laying of cable. Cart away, dispose excess as advised. | m | 150
5.9.2.2.02 | Excavate, expose and remove a section of existing DN75 GS Borehole-rising main inter-connection pipe work .Trim the trenching to size 500 mmWx600 mm depth. Back fill to ground level after laying of cable. Cart away, dispose excess as advised. | m | 5
5.9.3 | REHABILITATION OF MAINS POWER CONTROL SWITCHGEAR PANEL, ELECTRICAL WIRING OF SWITCHGEAR//OFFICE/STORE BUILDING AND FIRE FIGHTING EQUIPMENT
5.9.3.1 | MAINS POWER CONTROL SWITCHGEAR PANEL
5.9.3.1 | Open the mains power switchgear panel, carefully clean, dust and air blows the compartment.. | Item | 1
5.9.3.1 | Replace the existing 125 mps, 3 phase mccb (Legrand DPX 125) on power control switchgear panel feeding starter for Bh. No. 6.2 with one rated 63 amps | Nr | 1
5.9.3.1 | Install 3 phase, 415 vac surge arrestor equipment in the panel. | Nr | 1
5.9.3.1 | Install 15 Kvar, 3 phase, 415 vac, 4 step automatic power capacitor correction bank | Set | 1
5.9.3.2 | ELECTRICAL WIRING OF MAINS POWER CONTROL SWITCHGEAR/STORE/OFFICE BUILDING
5.9.3.2.01 | Remove the existing socket/lighting wiring. | LS | 1
5.9.3.2.02 | 20 mm diam. GS conduit fixed on the walls and roof members. The cost shall be inclusive of tees, bends, circular boxes with covers, other necessary accessories | m | 100
5.9.3.2.03 | 1.5 mm2 single copper cables (Red=130 m, Black=100 m , Green =100 m) laid in GS conduit and terminated at boh ends. | m | 330
5.9.3.2.04 | 2.5 mm2 single copper cables (Red=75 m, Black=75 m , Green =75 m) laid in GS conduit and terminated at both ends. | m | 225
5.9.3.2.05 | 10 amps, I way 2 gang switch (smc) as Mem, Crabtree or similar quality approved make c/w box and ss screws | Nr | 1
5.9.3.2.06 | 10 amps, I way 1 gang switch (smc) as Mem, Crabtree or similar quality approved make c/w box and ss screws | Nr | 2
5.9.3.2.07 | 13 amps, 240 vac, twin switched socket outlet (smc) as Mem, Crabtree or similar quality approved make c/w box stainless steel screws (ringmain circuit). | Nr | 4
5.9.3.2.08 | 36 wattsx1200 mmL single fluorescent lighting fitting, energy save, water tight (IP 20), metal body, corrossion resistant, power factor compensated, c/w tube, starter mounted on ceiling but 20 mm off the surface using 20 mm diam. GS coupler) | Nr | 4
5.9.3.2.09 | 20 wattsx300 mmL LED fluorescent lighting fitting (IP54), energy save, corrossion resistant, power factor compensated. | Nr | 4
5.9.3.2.10 | Masory earth rod chamber of internal size 250x250 x300 mmH extending 50 mm above the ground. It shall be constructed from 150x150x450 mmL masonry blocks (1:3:6). It shall be c/w 75 mm thick perforated cover (1:2:4). | Nr | 1
5.9.3.2.11 | D15x2.4 metre copper earth rod c/w clamp in a masonry chamber.. | Nr | 1
5.9.3.2.12 | 25 mm2 sc copper cable laid trench and connected to earth rod and main switchgear panel earth bond tape. | m | 5
5.9.3.2.13 | 32 amps, TPN + E (5-pin), 415 vac, socket outet (smc) c/w isolator, base and screw top lid, wired using 6 mm2 sc copper cables in 32 mm diameter GS conduit. | No. | 1
5.9.3.2.14 | Improve lightning protection system | LS | 4
5.9.3.3 | AC/DC POWER SUPPLY
5.9.3.3.01 | Floor stand supported, 240 ac, 2.5 amps/24 vdc, 20 amps continuosly rated converter fully protected (overload/short-circuit/reverse voltage and polarity etc c/w RJ45, RS232, RS485 ports, mcbs protected outputs to supply water meter, borehole water level measurement, rising main pressure measurement, PLC, Radio/Data Trans-Receiver Equipment. | SET | 1
5.9.3.3 | Fire Fighting Equipment
5.9.3.3.01 | 5 Kg Class ABC Powder steel cylinder fire extinguisher, c/w pressure gauge wall mounting steel bracket , operating instructions and accessories, fully charged. | Nr | 2
Total Page 7
TOTAL BHs 6.1 & 6.2:- CARRIED TO BILLL 5 SUMMARY SHEET

## 5.10_BH8.1,8.2
PART 5.10 - Electro-Mechanical Works & Pipeworks Borehole 8.1 & 8.2 (Site-Repairs)
5.10.1 | BOREHOLE NO. 8.2
ITEM | ITEM DESCRIPTION | UNIT | QTY | Rate(KES) | Amount(KES)
5.10.1.1 | Electro-Mechanical Works
Items below are given for assumed pump capacity, final specifications (e.g. cable thickness) and quantity are dependent on type of pump and pumping depths and have to be identified by the contractor after test pumping
SUPPLY, DELIVER TO SITE, INSTALL AND TEST:
NOTE:
5.10.1.1.01 | Submersible pump set of capacity 12 m3/hr. of water against a total head of 165 metres directly coupled to 3 phase, 415 vac motor, with pump suction inlet at 74 metres below ground level. | Nr | 1
5.10.1.1.02 | Overheads and profits on item 5.10.1.1.01 as specified for Prime Cost sum items | %
5.10.1.1.03 | 10 mm2/4 core submersible pump flat cable | m | 76
5.10.1.1.05 | DN6x120 mmL stainless steel water level control electrodes. | Pair | 1
5.10.1.1.06 | OD25 class D uPVC dipper pipe | m | 74
5.10.1.1.07 | DN50 GS class C threaded water pipe. | m | 74
5.10.1.1.08 | DN50 Steel steam sockets | Nr | 14
5.10.1.1.09 | DN65x300 mm long GS starter pipe | Nr | 1
5.10.1.1.10 | DN65x50 GS reducer (female threaded) | Nr | 1
5.10.1.1.11 | 0.75mm2 sc double insulated copper cable( brown and black) each 76 metres | m | 152
5.10.1.1.12 | Lay in trench/duct, connect and test 1.5 mm2/2c pvc swa pvc copper cable (starter panel to borehole) | m | 35
5.10.1.1.13 | Lay in trench/duct, connect and test 10 mm2/4c armoured copper cable | m | 35
5.10.1.1.14 | Copper cable gland c/w lock-nut and shroud for 10 mm2/4 core pvc swa pvc copper cable. | Nr | 2
5.10.1.1.15 | Copper cable gland c/w lock-nut and shroud for 1.5 mm2/2 core pvc swa pvc copper cable. | Nr | 2
5.10.1.1.16 | Supply and install water-tight GS cable junction box of size 150x150x90mm depth, fabricated from 3 mm thick plate.. It shall have GS DIN plate fixed at the inside centre but raised by 10 mm from back side. 3 No. 10 amps and 5 No. 30 amps cable terminal blocks mounted on the plate, tough rubber cable grommets for 10mm2/4c and 0.75 mm2 sc submerssible cable. | Nr | 1
5.10.1.1.17 | 10 Kw, 3 phase, 415 vac, soft starter panel including integral 3 phase surge arrestor unit. The cost shall be inclusive 10 mm2/4c armoured copper cable, cable glands etc for connection from starter panel to main switchgear. | SET | 1
5.10.1.1.18 | DN38x150 mmL GS threaded pipe piece (cable entry) | Nr | 1
5.10.1.1.19 | Supply and installation of Well Probe Sensor complete with well probe cable of size 0.75 mm² of 75 m (to be determined after test pumping). | SET | 1
5.10.1.1.20 | Supply, installation, testing and commissioning of Electro Magnetic Flow Meter, DN80, Qmax=80m3/hr, Qnom=40m3/hr, QT=8m3/hr and Qmin=1.2m3/hr, 2 battery power supply, IP 68, RS232 and RS 485 outputs. | Nr | 1
5.10.1.1.21 | Supply, installation, testing and commissioning of Hydrostatic Level Transmitter with integrated Pt 100 temperature sensor 0-700C, range from 1-100 mH2Og, acuracy + 0.175% FS BSL NLHR>4mH2O, +o.25%<4mH2O. | Nr | 1
TOTAL PAGE 1
5.10.1.1.22 | Installation Sundries
5.10.1.1.22a | ID320x4 mm Thick GS Borehole cap with welded DN50 GS pipe piece, welded DN38 GS slow bend for passage of 10mm2/4c cable, water level control electrodes cables and passage of OD25 mm pvc dipper pipe. | Nr | 1
5.10.1.1.22b | Boss white (200 gm tin) | pc | 2
5.10.1.1.22c | 450 mm plastic cable tie | Nr | 50
5.10.1.1.22d | 20 mm Wx9ML self bonding electrical tape (scotch 23) | ROLL | 2
5.10.1.1.22e | 12 mm Wx12 ML PTFE thread seal tape | ROLL | 10
5.10.1.1.22f | 20 mm high quality electrical pvc tape (Red, Yellow, Blue, Black) | ROLL | 4
5.10.1.1.22g | Stainless steel ferrules for 10mm2 cable | Nr | 4
5.10.1.1.22h | Stainless steel ferrules for 0.75 mm2 cable | Nr | 3
5.10.1.1.22i | 10 amps cable terminal block | Nr | 4
5.10.1.1.22j | 30 amps cable terminal block | Nr | 4
5.10.1.1.23 | Other Electro-mechanical Works - BH 8.3
5.10.1.1.23a | Preparation of all design technical and working drawings for the works for approval prior to commencement of installation of works as per the Specifications. | LS | 1
5.10.1.1.23b | Allow for all the builders works associated with all the electrical works that the contractor considers necessary to complete works | LS | 1
5.10.1.1.23c | Painting, varnishing and any other works necessary for making good all the disturbed areas as a result of the new electrical installations. | LS | 1
5.10.1.1.23d | Supply, installation, testing and commissioning of Amplified Pressure Transmitter with pressure range of 20 bar, over pressure safety of 50 bar, from SS material, and power supply 10<UCB<30 VDC and signal output 4-20 mA 2-wire system. | Nr | 1
5.10.1.1.23e | ID8x3 mm Thick GS tube c/w all necessary mounting fittings, bends etc enclosed in DN15 GS pipe for connection on GS rising main and laid in trenching/duct and connection on pressure switch, pressure gauge at the power supply control room. | m | 30
5.10.1.1.22f | Adjustable Pressure switch in IP54 metal enclosure, with dual scale (Kg/cm2 and Bar), range 0 - 25 Kg/cm2 (0 - 25 Bar) connected to GS copper tube and fixed firmly on the wall by GS bracket. It shall have integral 2NO+2NC auxillary contacts rated 10 amps, 240 vac, stainless steel isolation ball valve. | Nr | 1
5.10.1.1.23g | High quality pressure gauge - (indoor mounting), with dual scale (Kg/cm2 and Bar).Range (0 - 30 Kg/cm2 )/(0 - 30 bar). It shall be c/w all fitting accessories for connecting on ID8x3mm GS tube. It shall be c/w stainless steel isolation ball valve. | Nr | 1
5.10.1.1.22h | Single orifice cast steel air valve c/w accessories for mounting on DN75 GS pipe. | Nr | 1
5.10.1.1.22i | Supply, installation, testing and commissioning of 24V DC Power Supply Unit, 500VAC Equipped with one input fuse, 187 – 264 VAC, 47 to 63 Hz,0°C….+45°C,≥ IP20. | Nr | 1
5.10.1.1.22j | Supply, installation and testing of Input /Output interface module (I/O), min. 4 analog inputs 0-10V, 0-20mA, 4-20mA programmable, min 2 digital inputs with frequency range 0-16 Hz. | Nr | 1
5.10.1.1.23k | Supply, installation and testing of Class 10 GPRS Modem, Dual-Band E-GSM/GPRS 900/1800 MHz,GPRS multi-slot class 10,1W@900 MHz,1W@ 1800 MHz,Control via AT commands, -200 C to +550C,RS 232 interface,TCP/IP protocol stack for M2M | Nr | 1
5.10.1.1.23l | Supply and installation of 1.5mm² armoured underground cable for the well probe | m | 30
5.10.1.1.24 | Pressure Pipes and Fittings:
Modification of the connection between the new pump, the suction and the discharge pipes and fittings, and for corresponding concrete works.
5.10.1.1.24a | Disconnection, dismantling and disposal of old pipes, pipe fittings, valves, water meter. | LS | 1
TOTAL PAGE 2
Supply, delivery to Site, Install and Test:
5.10.1.1.24b | DN50x90o GI slow bend with a bore for pressure gauge | Nr | 1
5.10.1.1.24c | DN50 GI socket with bore for mounting air valve | Nr | 1
5.10.1.1.24d | DN75x50 GI reducer (female threaded) | Nr | 1
5.10.1.1.24e | DN50x1500 GI pipe piece (threaded at both ends) | Nr | 1
5.10.1.1.24f | DN50x300 GI pipe piece )(threaded at both ends | Nr | 1
5.10.1.1.24g | DN50x90o GI slow bend | Nr | 2
5.10.1.1.24h | DN50 GI hex nipple | Nr | 4
5.10.1.1.24i | DN50 GS union | Nr | 3
5.10.1.1.24k | DN50 stainless steel Non-Return. | Nr | 1
5.10.1.1.24l | DN75 steel Johnson coupling c/w rubber rings, bolts, washers and nuts | Nr | 2
5.10.1.2 | Removal Of Old Items and Trenching
5.10.1.2.01 | Excavate, expose and remove existing cables ( power control room to borehole). Trim the trenching to size 450 mmWx500 mm depth. Back fill to ground level after laying of cable. Cart away, dispose excess as advised. | m | 35
5.10.1.2.02 | Excavate, expose and remove a section of existing DN50 GI Borehole-rising main inter-connection pipe work. Trim the trenching to size 500 mmWx600 mm depth. Back fill to ground level after laying of pipe. Cart away, dispose excess as advised. | m | 5
5.10.2 | BOREHOLE NO. 8.1
5.10.2.1 | Electro-Mechanical Works
Items below are given for assumed pump capacity, final specifications (e.g. cable thickness) and quantity are dependent on type of pump and pumping depths and have to be identified by the contractor after test pumping
5.10.2.1.01 | Remove pump set and drop pipes (Grundfos SP30-21, DN75 GI, Pump inlet depth = 75 metres below ground level | LS | 1
SUPPLY, DELIVER TO SITE, INSTALL AND TEST:
NOTE:
5.10.2.1.02 | Submersible pump set of capacity 23 m3/hr. of water against a total head of 175 metres directly coupled to 3 phase, 415 vac motor, with pump suction inlet at 73 metres below ground level. | Nr | 1
5.10.2.1.03 | Overheads and profits on item 5.10.2.1.02 as specified for Prime Cost sum items | %
5.10.2.1.04 | 16 mm2/4 core submersible pump flat cable | m | 76
5.10.2.1.05 | DN6x120 mmL stainless steel water level control electrodes. | Pair | 1
5.10.2.1.06 | OD25 class D uPVC dipper pipe | m | 74
5.10.2.1.07 | DN75 GS class C threaded water pipe. | m | 74
5.10.2.1.08 | DN75 Steel steam sockets | Nr | 15
5.10.2.1.09 | DN75x300 mm long GS starter pipe | Nr | 1
5.10.2.1.10 | DN100x75 GS reducer (female threaded) | Nr | 1
5.10.2.1.11 | 0.75mm2 sc double insulated copper cable( brown and black) each 75 metres | m | 152
5.10.2.1.12 | Lay in trench/duct, connect and test 1.5 mm2/2c pvc swa pvc copper cable (starter panel to borehole) | m | 25
5.10.2.1.13 | Lay in trench/duct, connect and test 16 mm2/4c armoured copper cable | m | 25
5.10.2.1.14 | Copper cable gland c/w lock-nut and shroud for 16 mm2/4 core pvc swa pvc copper cable. | Nr | 2
5.10.2.1.15 | Copper cable gland c/w lock-nut and shroud for 1.5 mm2/2 core pvc swa pvc copper cable. | Nr | 2
5.10.2.1.16 | Masory earth rod chamber of internal size 250x250 x300 mmH extending 50 mm above the ground. It shall be constructed from 150x150x450 mmL masonry blocks (1:3:6). It shall be c/w 75 mm thick perforated cover (1:2:4). | Nr | 1
5.10.2.1.17 | D15x2.4 metre copper earth rod c/w clamp in a masonry chamber. | Nr | 1
5.10.2.1.18 | 16 mm2 sc copper cable (green) | m | 5
5.10.2.1.19a | Supply and install water-tight GS cable junction box of size 150x150x90mm depth, fabricated from 3 mm thick plate. It shall have GS DIN plate fixed at the inside centre but raised by 10 mm from back side. 3 No. 10 amps and 5 No.60 amps cable terminal blocks mounted on the plate, tough rubber cable grommets for 16mm2/4c and 0.75 mm2 sc submerssible cable. | Nr | 1
5.10.2.1.1b | DN38x150 mmL GS threaded pipe piece (cable entry) | Nr | 1
5.10.2.1.20 | 18.5 Kw, 3 phase, 415 vac, soft starter panel including integral 3 phase surge arrestor unit. | SET | 1
TOTAL PAGE 3
5.10.2.1.21 | Supply and installation of Well Probe Sensor complete with well probe cable of size 0.75 mm² of 76 m (to be determined after test pumping). | SET | 1
5.10.2.1.22 | Supply, installation, testing and commissioning of Electro Magnetic Flow Meter, DN80, Qmax=80m3/hr, Qnom=40m3/hr, QT=8m3/hr and Qmin=1.2m3/hr, 2 battery power supply, IP 68, RS232 and RS 485 outputs. | Nr | 1
5.10.2.1.23 | Supply, installation, testing and commissioning of Hydrostatic Level Transmitter with integrated Pt 100 temperature sensor 0-700C, range from 1-100 mH2Og, acuracy + 0.175% FS BSL NLHR>4mH2O, +o.25%<4mH2O. | Nr | 1
5.10.2.1.24 | Installation Sundries
5.10.2.1.24a | ID220x4 mm Thick GS Borehole cap with welded DN75 GS pipe piece, welded DN38 GI slow bend for passage of 16mm2/4c cable, water level control electrodes cables and passage of OD25 mm pvc dipper pipe. | Nr | 1
5.10.2.1.24b | Boss white (200 gm tin) | Pc | 2
5.10.2.1.24c | 450 mm plastic cable tie | Nr | 50
5.10.2.1.24d | 20 mm Wx9ML self bonding electrical tape (scotch 23) | ROLL | 2
5.10.2.1.24e | 12 mm Wx12 ML PTFE thread seal tape | ROLL | 10
5.10.2.1.24f | 20 mm high quality electrical pvc tape (Red, Yellow, Blue, Black) | ROLL | 4
5.10.2.1.24g | Stainless steel ferrules for 16mm2 cable | Nr | 4
5.10.2.1.24h | Stainless steel ferrules for 0.75 mm2 cable | Nr | 2
5.10.2.1.24i | 10 amps cable terminal block | Nr | 3
5.10.2.1.24j | 30 amps cable terminal block | Nr | 4
5.10.2.1.25 | Other Electro-mechanical Works - BH 8.1
5.10.2.1.25a | Preparation of all design technical and working drawings for the works for approval prior to commencement of installation of works as per the Specifications. | LS | 1
5.10.2.1.25b | Allow for all the builders works associated with all the electrical works that the contractor considers necessary to complete works. | LS | 1
5.10.2.1.25c | Painting, varnishing and any other works necessary for making good all the disturbed areas as a result of the new electrical installations. | LS | 1
5.10.2.1.25d | Supply, installation, testing and commissioning of Amplified Pressure Transmitter with pressure range of 20 bar, over pressure safety of 50 bar, from SS material, and power supply 10<UCB<30 VDC and signal output 4-20 mA 2-wire system. | Nr | 1
5.10.2.1.25e | ID8x3 mm Thick GS tube c/w all necessary mounting fittings, bends etc enclosed in DN15 GS pipe for connection on GS rising main and laid in trenching/duct and connection on pressure switch, pressure gauge at the power supply control room. | m | 20
5.10.2.1.25f | Adjustable Pressure switch in IP54 metal enclosure, with dual scale (Kg/cm2 and Bar), range 0 - 25 Kg/cm2 (0 - 25 Bar) connected to GS copper tube and fixed firmly on the wall by GS bracket. It shall have integral 2NO+2NC auxillary contacts rated 10 amps, 240 vac, stainless steel isolation ball valve. | Nr | 1
5.10.2.1.25g | High quality pressure gauge - (indoor mounting), with dual scale (Kg/cm2 and Bar).Range (0 - 30 Kg/cm2 )/(0 - 30 bar). It shall be c/w all fitting accessories for connecting on ID8x3mm GS tube. It shall be c/w stainless steel isolation ball valve. | Nr | 1
5.10.2.1.25h | Single orifice cast steel air valve c/w accessories for mounting on DN75 GS pipe. | Nr | 1
5.10.2.1.25i | Supply, installation, testing and commissioning of 24V DC Power Supply Unit, 500VAC Equipped with one input fuse, 187 – 264 VAC, 47 to 63 Hz,0°C….+45°C,≥ IP20. | Nr | 1
TOTAL PAGE 4
5.10.2.1.25j | Supply, installation and testing of Input /Output interface module (I/O), min. 4 analog inputs 0-10V, 0-20mA, 4-20mA programmable, min 2 digital inputs with frequency range 0-16 Hz | Nr | 1
5.10.2.1.25k | Supply, installation and testing of Class 10 GPRS Modem, Dual-Band E-GSM/GPRS 900/1800 MHz,GPRS multi-slot class 10,1W@900 MHz,1W@ 1800 MHz,Control via AT commands, -200 C to +550C,RS 232 interface,TCP/IP protocol stack for M2M | Nr | 1
5.10.2.1.25l | Supply and installation of 1.5mm² armoured underground cable for the well probe | m | 20
5.10.2.1.26 | Pressure Pipes and Fittings:
Modification of the connection between the new pump, the suction and the discharge pipes and fittings, and for corresponding concrete works.
5.10.2.1.26a | Disconnection, dismantling and disposal of old pipes, pipe fittings, valves, water meter. | LS | 1
Supply, delivery to Site, Install and Test:
5.10.2.1.26b | DN75x90o GS slow bend with a bore for pressure gauge | Nr | 1
5.10.2.1.26c | DN75 GS socket with bore for mounting air valve | Nr | 1
5.10.2.1.26d | DN75x50 GS reducer (threaded) | Nr | 1
5.10.2.1.26e | DN75x1500 GS pipe piece (threaded at both ends) | Nr | 1
5.10.2.1.26f | DN75x300 GS pipe piece )(threaded at both ends | Nr | 1
5.10.21.26g | DN75x90o GS slow bend | Nr | 2
5.10.2.1.26h | DN75 CS hex nipple | Nr | 4
5.10.2.1.26i | DN75 GS union (threaded) | Nr | 3
5.`0.2.1.26j | DN75 stainless steel non-slam, Non-Return valve (threaded) | Nr | 1
5.10.2.1.26k | DN75 steel Johnson coupling c/w rubber rings. | Nr | 3
5.10.2.1.26l | DN75xPN20 gate valve c/w handwheel. | Nr | 2
5.10.2.1.26m | DN75, PN 20 bar Y-strainer | Nr | 1
5.10.2.1.26n | DN100x75 GS reducer | Nr | 2
5.10.2.1.26o | DN100x200 mmL GS pipe piece | Nr | 2
5.10.2.1.26p | DN100x250 mmL GS pie piece | Nr | 2
5.10.2.1.26q | DN100 steel Johnson coupling c/w rubber rings. | Nr | 2
5.10.2.1.26r | DN100xPN20 gate valve c/w handwheel. | Nr | 1
5.10.2.2 | Removal Of Old Items and Trenching
5.10.2.2.01 | Excavate, expose and remove existing cables ( power control room to borehole). Trim the trenching to size 450 mmWx500 mm depth. Back fill to ground level after laying of cable. Cart away, dispose excess as advised. | m | 20
5.10.2.2.02 | Excavate, expose and remove a section of existing DN75 GIS Borehole-rising main inter-connection pipe work .Trim the trenching to size 500 mmWx600 mm depth. Back fill to ground level after laying of pipe. Cart away, dispose excess as advised. | m | 3
TOTAL PAGE 5
5.10.3 | REHABILITATION OF MAINS POWER CONTROL SWITCHGEAR PANEL, ELECTRICAL WIRING OF SWITCHGEAR/OFFICE BUILDING AND FIRE FIGHTING EQUIPMENT
5.10.3.1 | MAINS POWER CONTROL SWITCHGEAR PANEL
5.10.3.1.01 | Open the mains power switchgear panel, carefully clean, dust and air blows the compartment.. | ITEM | 1
5.10.3.1.02 | Replace the existing 125 mps, 3 phase mccb on power control switchgear panel feeding starter for BH. No. 8.2 with one rated 63 amps | Nr | 1
5.10.3.1.03 | Install 3 phase, 415 vac surge arrestor equipment in the panel. | Nr | 1
5.10.3.1.04 | Install 18 Kvar, 3 phase, 415 vac, 4 step automatic power capacitor correction bank | SET | 1
5.10.3.1.05 | 3x2.5 mm2 single core copper cables wired in 20 mm diameter pvc conduit from consumer unit to fan speed control unit and fan terminals. | m | 6
5.10.3.1.06 | Remove the defective cooling fan. Install a new one rated 25 watts, 240 vac at 100 mm height from the bottom of the panel c/w dust-prooof filter and protective GS wire frame (2x2xD1.5 mm). Install where the defective fan has been removed from, protective GS grid (2x2xD1.5 mm) c/w filter . | SET | 1
5.10.3.2 | ELECTRICAL WIRING OF MAINS POWER CONTROL SWITCHGEAR/ OFFICE BUILDING
5.10.3.2.01 | Remove the existing socket/lighting wiring. | LS | 1
5.10.3.2.02 | 20 mm diam. GS conduit fixed on the walls and roof members. The cost shall be inclusive of tees, bends, circular boxes with covers, other necessary accessories | m | 28
5.10.3.2.03 | 1.5 mm2 single copper cables (Red=50 m, Black=25 m , Green =25 m) laid in GS conduit and terminated at boh ends. | m | 90
5.10.3.2.04 | 2.5 mm2 single copper cables (Red=25 m, Black=25 m , Green =25 m) laid in GS conduit and terminated at boh ends. | m | 75
5.10.3.2.05 | 10 amps, 1I way 2 gang switch (smc) as Mem, Crabtree or similar quality approved make c/w box and ss screws | Nr | 1
5.10.3.2.06 | 10 amps, 1 way 1 gang switch (smc) as Mem, Crabtree or similar quality approved make c/w box and ss screws | Nr | 1
5.10.3.2.07 | 13 amps, 240 vac, twin switched socket outlet (smc) as Mem, Crabtree or similar quality approved make c/w box stainless steel screws (ringmain circuit). | Nr | 2
5.10.3.2.08 | 36 wattsx1200 mmL single fluorescent lighting fitting, energy save, water tight (IP 20), metal body, corrossion resistant, power factor compensated, c/w tube, starter mounted on ceiling but 20 mm off the surface using 20 mm diam. GS coupler) | Nr | 2
5.10.3.2.09 | 20 wattsx300 mmL LED fluorescent lighting fitting (IP54), energy save, corrossion resistant, power factor compensated. | Nr | 4
5.10.3.2.10 | 3x2.5 mm2 single core copper cables wired in 20 mm diameter pvc conduit from consumer unit to fan speed control unit and fan terminals. | m | 6
5.10.3.2.11 | 3 blade, adjustable slow speed (0-300 rpm), 240 vac ceiling mounted cooling fan c/w speed adjustable control unit completely wired (in conduit). | SET | 1
5.10.3.2.12 | 32 amps, TPN + E (5-pin), 415 vac, socket outet (smc) c/w isolator, base and screw top lid, wired using 6 mm2 sc copper cables in 32 mm diameter GS conduit. | No | 1
5.10.3.2.13 | Improve lightning protection system | LS | 3
5.10.3.3 | AC/DC POWER SUPPLY
5.10.3.3.01 | Floor stand supported, 240 ac, 2.5 amps/24 vdc, 20 amps continuosly rated converter fully protected (overload/short-circuit/reverse voltage and polarity etc c/w RJ45, RS232, RS485 ports, mcbs protected outputs to supply water meter, borehole water level measurement, rising main pressure measurement, PLC, Radio/Data Trans-Receiver Equipment. | SET | 1
5.10.3.3 | FIRE FIGHTING EQUIPMENT
5.10.3.3.1 | 5 Kg Class ABC Powder steel cylinder fire extinguisher, c/w pressure gauge wall mounting steel bracket , operating instructions and accessories, fully charged. | Nr | 2
TOTAL PAGE 6
TOTAL BHs 8.1, 8.2, 8.3 :- CARRIED TO BILLL 5 SUMMARY SHEET

## 5.11_BH9
PART 5.11 - Electro-Mechanical Works & Pipeworks Borehole 9 (Site-Replacement)
5.11.1 | BOREHOLE NO. 9
ITEM | ITEM DESCRIPTION | UNIT | QTY | Rate(KES) | Amount(KES)
5.11.1.1 | Electro-Mechanical Works
Items below are given for assumed pump capacity, final specifications (e.g. cable thickness) and quantity are dependent on type of pump and pumping depths and have to be identified by the contractor after test pumping.
SUPPLY, DELIVER TO SITE, INSTALL AND TEST:
NOTE:
5.11.1.1.01 | Submersible pump set of capacity 9 m3/hr. of water against a total head of 150 metres directly coupled to 3 phase, 415 vac motor, with pump suction inlet at 66 metres below ground level c/w cable guard. | Nr | 1
5.11.1.1.02 | Overheads and profits on item 5.11.1.1.01 as specified for Prime Cost sum items | %
5.11.1.1.03 | 6 mm2/4 core submersible pump flat cable | m | 70
5.11.1.1.05 | DN6x120 mmL stainless steel water level control electrodes. | Pair | 1
5.11.1.1.06 | OD25 class D uPVC dipper pipe | m | 66
5.11.1.1.07 | DN50 GS class C threaded water pipe. | m | 65
5.11.1.1.08 | DN50 Steel steam sockets | Nr | 14
5.11.1.1.09 | DN50x300 mm long GS starter pipe | Nr | 1
5.11.1.1.11 | 0.75mm2 sc double insulated copper cable( brown and black) each 76 metres | m | 140
5.11.1.1.12 | Lay in trench/duct, connect and test 1.5 mm2/2c pvc swa pvc copper cable (starter panel to borehole) | m | 15
5.11.1.1.13 | Lay in trench/duct, connect and test 6 mm2/4c armoured copper cable | LM | 15
5.11.1.1.14 | Copper cable gland c/w lock-nut and shroud for 6 mm2/4 core pvc swa pvc copper cable. | Nr | 2
5.11.1.1.15 | Copper cable gland c/w lock-nut and shroud for 1.5 mm2/2 core pvc swa pvc copper cable. | Nr | 2
5.11.1.1.16 | Supply and install water-tight GS cable junction box of size 150x150x90mm depth, fabricated from 3 mm thick plate.. It shall have GS DIN plate fixed at the inside centre but raised by 10 mm from back side. 3 No. 10 amps and 5 No. 30 amps cable terminal blocks mounted on the plate, tough rubber cable grommets for 10mm2/4c and 0.75 mm2 sc submerssible cable. | Nr | 1
5.11.1.1.17 | 7.5 Kw, 3 phase, 415 vac,Direct-On Line starter panel (smc,DIN, wall mounted). It shall comprise of the following componennts amoung others, fully wired and labeled (powerand control wiring drawings must be submitted): including integral 3 phase surge arrestor unit, 32 amps Tpn Isolator with door rotary handle, amps 32 amps tpn class B mcb, LED pilot indicatotor lights (Green = Run, Red = Overload Tripped, Amber= BH Level Low, Yellow= Discharge Pressure High), Start, Stop/Rest push buttons, Hours Counter, Over/Under Voltage and Phase Failure Relay, Thermal Overload relay range 16-19-22 amps Set at 19 amps, Water level control relay, 10No. 10 amps, 8 No. 30 ambs cable terminal blocks firmly fixed on GS bracket mounted near the bottom etc | SET | 1
TOTAL PAGE 1
5.11.1.1.18 | Installation Sundries
5.10.1.1.22 | Installation Sundries
5.11.1.1.18a | ID320x4 mm Thick GS Borehole cap with welded DN50 GS pipe piece, welded DN38 GS slow bend for passage of 10mm2/4c cable, water level control electrodes cables and passage of OD25 mm pvc dipper pipe. | Nr | 1
5.11.1.1.18b | Boss white (200 gm tin) | pc | 2
5.11.1.1.18c | 400 mm plastic cable tie | Nr | 40
5.11.1.1.18d | 20 mm Wx9ML self bonding electrical tape (scotch 23) | ROLL | 2
5.11.1.1.18e | 12 mm Wx12 ML PTFE thread seal tape | ROLL | 10
5.11.1.1.18f | 20 mm high quality electrical pvc tape (Red, Yellow, Blue, Black) | ROLL | 4
5.11.1.1.18g | Stainless steel ferrules for 6 mm2 cable | Nr | 4
5.11.1.1.18h | Stainless steel ferrules for 0.75 mm2 cable | Nr | 3
5.11.1.1.18j | DN38x150 mmL GS threaded pipe piece (cable entry) | Nr | 1
5.11.1.1.19 | Other Electro-mechanical Works - BH 9
5.11.1.1.19a | Preparation of all design technical and working drawings for the works for approval prior to commencement of installation of works as per the Specifications. | LS | 1
5.11.1.1.19b | Allow for all the builders works associated with all the electrical works that the contractor considers necessary to complete works | LS | 1
5.11.1.1.19c | Painting, varnishing and any other works necessary for making good all the disturbed areas as a result of the new electrical installations. | LS | 1
5.11.1.1.19d | Supply, installation, testing and commissioning of Amplified Pressure Transmitter with pressure range of 20 bar, over pressure safety of 50 bar, from SS material, and power supply 10<UCB<30 VDC and signal output 4-20 mA 2-wire system. | Nr | 1
5.11.1.1.`19e | Supply and installation of Well Probe Sensor complete with well probe cable of size 0.75 mm² of 75 m (to be determined after test pumping). | SET | 1
5.11.1.1.19f | Supply, installation, testing and commissioning of Electro Magnetic Flow Meter, DN80, Qmax=80m3/hr, Qnom=40m3/hr, QT=8m3/hr and Qmin=1.2m3/hr, 2 battery power supply, IP 68, RS232 and RS 485 outputs. | Nr | 1
5.11.1.1.19g | Supply, installation, testing and commissioning of Hydrostatic Level Transmitter with integrated Pt 100 temperature sensor 0-700C, range from 1-100 mH2Og, acuracy + 0.175% FS BSL NLHR>4mH2O, +o.25%<4mH2O. | Nr | 1
5.11.1.1.19h | ID8x3 mm Thick GS tube c/w all necessary mounting fittings, bends etc enclosed in DN15 GS pipe for connection on GS rising main and laid in trenching/duct and connection on pressure switch, pressure gauge at the power supply control room. | m | 30
5.11.1.1.19i | Adjustable Pressure switch in IP54 metal enclosure, with dual scale (Kg/cm2 and Bar), range 0 - 25 Kg/cm2 (0 - 25 Bar) connected to GS copper tube and fixed firmly on the wall by GS bracket. It shall have integral 2NO+2NC auxillary contacts rated 10 amps, 240 vac, stainless steel isolation ball valve. | Nr | 1
5.11.1.1.19j | High quality pressure gauge - (indoor mounting), with dual scale (Kg/cm2 and Bar).Range (0 - 30 Kg/cm2 )/(0 - 30 bar). It shall be c/w all fitting accessories for connecting on ID8x3mm GS tube. It shall be c/w stainless steel isolation ball valve. | Nr | 1
5.11.1.1.19k | Single orifice cast steel air valve c/w accessories for mounting on DN75 GS pipe. | Nr | 1
5.11.1.1.19l | Supply, installation, testing and commissioning of 24V DC Power Supply Unit, 500VAC Equipped with one input fuse, 187 – 264 VAC, 47 to 63 Hz,0°C….+45°C,≥ IP20. | Nr | 1
5.11.1.1.19m | Supply, installation and testing of Input /Output interface module (I/O), min. 4 analog inputs 0-10V, 0-20mA, 4-20mA programmable, min 2 digital inputs with frequency range 0-16 Hz. | Nr | 1
TOTAL PAGE 2
5.11.1.1.19n | Supply, installation and testing of Class 10 GPRS Modem, Dual-Band E-GSM/GPRS 900/1800 MHz,GPRS multi-slot class 10,1W@900 MHz,1W@ 1800 MHz,Control via AT commands, -200 C to +550C,RS 232 interface,TCP/IP protocol stack for M2M | No | 1
5.11.1.1.19o | Supply and installation of 1.5mm² armoured underground cable for the well probe | m | 15
5.11.1.1.20 | Pressure Pipes and Fittings:
Modification of the connection between the new pump, the suction and the discharge pipes and fittings, and for corresponding concrete works.
5.11.1.1.20a | Disconnection, dismantling and disposal of old pipes, pipe fittings, valves, water meter. | LS | 1
Supply, delivery to Site, Install and Test:
5.11.1.1.20b | DN50x90o GS slow bend with a bore for pressure gauge/switch | Nr | 1
5.11.1.1.20c | DN75 GS socket with bore for mounting air valve | Nr | 1
5.11.1.1.20d | DN75x50 GS reducer (female threaded) | Nr | 1
5.11.1.1.20e | DN50x1500 GS pipe piece (threaded at both ends) | Nr | 1
5.11.1.1.20f | DN50x300 GS pipe piece (threaded at both ends) | Nr | 2
5.11.1.1.20g | DN50x90o GS slow bend | Nr | 2
5.11.1.1.20h | DN50 GS hex nipple | Nr | 4
5.11.1.1.20i | DN50 GS union | Nr | 3
5.11.1.1.20k | DN50 steel non-slam, Non-Return.(threaded) | Nr | 1
5.11.1.1.20l | DN75 steel Johnson coupling c/w rubber rings, bolts, washers and nuts | Nr | 2
5.11.1.1.20m | DN75x2500 mmL GS pipe piece (threaded at both ends) | Nr | 2
5.11.1.1.20n | DN75 GS equal Tee (threaded) | Nr | 1
5.11.1.1.20o | DN75x1500 mmL GS pipe piece (threaded at both ends) | Nr | 2
5.11.1.1.20p | DN75 GS union | Nr | 2
5.11.1.1.20q | DN75 GS hex nipple | Nr | 3
5.11.1.1.20r | DN75 GS GS elbow | Nr | 2
5.11.1.1.20r | DN75xPN20 gate valve c/w handwheel | Nr | 2
5.11.1.1.2 | Removal Of Old Items and Trenching
5.11.1.1.2.01 | Excavate, expose and remove existing cables ( power control room to borehole). Trim the trenching to size 450 mmWx500 mm depth. Back fill to ground level after laying of cable. Cart away, dispose excess as advised. | m | 10
5.11.1.1.2.02 | Excavate, expose and remove a section of existing DN75 GI Borehole-rising main inter-connection pipe work. Trim the trenching to size 500 mmWx600 mm depth. Back fill to ground level after laying of pipe. Cart away, dispose excess as advised. | m | 6
TOTAL PAGE 3
5.11.1.3. MAINS POWER CONTROL SWITCHGEAR PANEL, ELECTRICAL
WIRING OF SWITCHGEAR/OFFICE/CHEMICAL DOSING BUILDING
AND FIRE FIGHTING EQUIPMENT
5.11.1.3.1 | NEW MAINS POWER CONTROL SWITCHGEAR PANEL
5.11.1.3.01 | Pick the existing free standing switchgear panel existing on site, remove the existing components,repair, clean, air blow the panel, apply two coats of paint on both the interior and exterior surfaces. | Nr | 1
5.11.1.3.02 | Supply,install, wire and test the following items in the panel ( see other new switchgear panels at other borehole sites); | Nr | 1
5.11.3.1.03 | Kenya Power & Lighting Company CUT-OUTS chamber | Nr | 1
5.11.3.1.04 | 1xKPLC incommer Current transformers chamber | Nr | 1
5.11.3.1.05 | 1xKPLC metering equipment chamber incommer Current transformers chamber | Nr | 1
5.11.3.1.06 | 1x250 amps adjustable triple pole mccb (adjustable range: 0.7IN, 0.8IN, 0.9IN, 1.0IN set at 0.8IN where IN= rated current of mccb = 250 amps). | Nr | 1
5.11.3.1.07 | 1x7.5 Kvar, 3 phase, 415 vac, 5 step central automatic power capacitor correction bank c/w 40 amps TP supply mccb, contactors, fuses, programmable electronic PF controller.relay. 154 µF/phase etc. | Nr | 1
5.11.3.1.08 | 1xsingle phase, 240 vac kWh energy registering meter) | Nr | 1
5.11.3.1.09 | 4x260 amps high conductivity rectangular bare copper bus-bar conductors | Nr | 1
5.11.3.1.10 | 1x125 amps, TP, 415 vac, mccbs, ICU =25 kA. Each in its own cmpartment (1 No. for Borehole No.4, 1 No. for BH No.7, and 2 No. spares. | Nr | 1
5.11.3.1.11 | 2x63 amps, TP, 415 vac, mccbs, ICU =15 kA. Each in its own cmpartment. (Spares) | Nr | 1
5.11.3.1.12 | 1x3 phase, 415 vac surge divertor c/w protective mcbs on main 250 amps mccb | Nr | 1
5.11.3.1.13 | 1x100 amps,1phase, 240 vac class "A" mcbs (staff houses - future) | Nr | 1
5.11.3.1.14 | 240 ac/24 vdc, 6 amps continuosly rated output converter fully protected | Nr | 1
5.11.3.1.15 | 1xCooling fan rated 25 watts, 240 vac, 2800 rpm continuously rated installed on the side, 100 mm height from the bottom clw filter and termite-proof, dust-proof stainless steel protection D1.5 mm wiregauze. | Nr | 1
5.11.3.1.16 | 2x ventillation hole of size 150x100 mm installed on the top opposite sides, 50 mm below top c/w termite-proof, dust-proof filter and grid. | Nr | 1
5.11.3.1.17 | 1x3 phase, 240 vac resettable digital network analyzer/recorder (voltage, current, kWh, Kva, Pf,Hz, Kw) with LED phase indicators (RED, YELLOW, BLUE) on front panel. | Nr | 1
5.11.3.1.18 | 100 amps, 6 way, 1 phase, 240 vac DIN distribution board; c/w; 2 No. 10 amps,1 pole, 240 vac class "A" mcbs, 3 No. 20 amps, 1 pole class "A" mcbs, 1 No. Blanking plate. | Nr | 1
5.11.3.1.19 | 3xAC ammeters range 0-300 amps c/w CTS. | Nr | 1
5.11.3.1.20 | 1xAC voltmeter (0-500 vac) c/w vss and protection mcbs. | Nr | 1
5.11.3.1.21 | 250 amps, 415 vac TPN manual changer-over switch c/w pilot indicator lights ( KPLC ON, KPLC LOAD ON, GENERATOR ON, GENERATOR LOAD ON) | Nr | 1
5.11.3.1.22 | 25x3 mm thick copper strip bound along the switchgear panel length (earthing) | SET | 1
5.11.3.2 | ELECTRICAL WIRING OF MAINS POWER CONTROL SWITCHGEAR/OFFICE BUILDING
5.11.3.2.01 | Remove the existing socket/lighting wiring. | LS | 1
5.11.3.2.02 | 20 mm diam. GS conduit fixed on the walls and roof members. The cost shall be inclusive of tees, bends, circular boxes with covers, other necessary accessories | m | 28
5.11.3.2.03 | 1.5 mm2 single copper cables (Red=50 m, Black=25 m , Green =25 m) laid in GS conduit and terminated at boh ends. | m | 90
5.11.3.2.04 | 2.5 mm2 single copper cables (Red=25 m, Black=25 m , Green =25 m) laid in GS conduit and terminated at boh ends. | m | 75
5.11.3.2.05 | 10 amps, 1I way 2 gang switch (smc) as Mem, Crabtree or similar quality approved make c/w box and ss screws | Nr | 1
5.11.3.2.06 | 10 amps, 1 way 1 gang switch (smc) as Mem, Crabtree or similar quality approved make c/w box and ss screws | Nr | 1
5.11.3.2.07 | 13 amps, 240 vac, twin switched socket outlet (smc) as Mem, Crabtree or similar quality approved make c/w box stainless steel screws (ringmain circuit). | Nr | 2
5.11.3.2.08 | 36 wattsx1200 mmL single fluorescent lighting fitting, energy save, water tight (IP 20), metal body, corrossion resistant, power factor compensated, c/w tube, starter mounted on ceiling but 20 mm off the surface using 20 mm diam. GS coupler) | Nr | 2
5.11.3.2.09 | 20 wattsx300 mmL LED fluorescent lighting fitting (IP54), energy save, corrossion resistant, power factor compensated. | Nr | 4
TotalPage 4
5.11.3.2.10 | 3x2.5 mm2 single core copper cables wired in 20 mm diameter pvc conduit from consumer unit to fan speed control unit and fan terminals. | m | 6
5.11.3.2.11 | 3 blade, adjustable slow speed (0-300 rpm), 240 vac ceiling mounted cooling fan c/w speed adjustable control unit completely wired (in conduit). | SET | 1
5.11.3.2.12 | Improve lightning protection system | LS | 1
5.11.3..3 | AC/DC POWER SUPPLY
5.11.3..3.01 | Floor stand supported, 240 ac, 2.5 amps/24 vdc, 20 amps continuosly rated converter fully protected (overload/short-circuit/reverse voltage and polarity etc c/w RJ45, RS232, RS485 ports, mcbs protected outputs to supply water meter, borehole water level measurement, rising main pressure measurement, PLC, Radio/Data Trans-Receiver Equipment. | SET | 1
5.11.3.3 | FIRE FIGHTING EQUIPMENT
5.11.3.3.1 | 5 Kg Class ABC Powder steel cylinder fire extinguisher, c/w pressure gauge wall mounting steel bracket , operating instructions and accessories, fully charged. | Nr | 2
TOTAL PAGE 5
TOTAL BH 9:- CARRIED TO BILLL 5 SUMMARY SHEET

## 5.12-Moni System
PART 5.12 - Tiwi Boreholes Monitoring System
ITEM | DESCRIPTION | UNIT | QTY | Rate(KES) | Amount(KES)
5.12 | SUPPLY INSTALLTION TESTING AND COMMISSIONING OF REMOTE MONITORING SYSTEM
5.12.1 | Supply, installation and testing of Local Server, minimum 32 Bit Microcontroller platform, Internal storage memory, Min. 21”LCD display,140VAC – 315VAC Phase to Neutral, 240VAC-VAC phase to phase, Keypad for user interaction Build in Ethernet Media Converter, multy-mode or single mode models with ST or SC connectors. Built in Ethernet Switch and Communication Module, 10-48 VDC power input with removable terminal blocks, inputs 10/100MB Ethernet, outputs RS232 and RS485 | Nr | 1
5.12.2 | UPS , 240V, back-up 8 hours | Nr | 1
5.12.3 | Supply, installation and testing of Software for Local Server | Nr | 1
5.12.4 | Cabling in Local Control Room | Nr | 1
5.12.5 | GPRS/GSM module | Nr | 1
NOTES
The monitoring system shall;
1. Cover 40 No. boreholes and 1 No. reservoir clustered within a radius of 50 Kms.
2. Interrogate the sites, issue instructions, obtain the information required through wireless communicaion.
3. DATA TO BE CAPTURED AT EACH BOREHOLE/RESERVOIR SITE:
At each site, the following information will be automatically collected and stored in memmory.
Continuous monitoring, recording and Storing data on:
3a). Water level in the borehole or reservoir.
3b). Pressure on the rising main from borehole/reservoir.
3c). System power consumption (KWh, Kw, KVA demand, Line Current, Line voltage, power factor,
supply frequency etc).
3d). Water flow rate (m3/hr or Litres/minute) and Cummulative quantity (M3 or litres) from water meter
of each borehole or reservoir.
3e). Status of the Pump set (Run, Stopped, Fault).
| TOTAL CARRIED TO BILLL 5 SUMMARY SHEET |  |  |  | 0

## 5.13-Solar PV
PART 5.13 - PROVISIONAL BILL: Solar Photo Voltaic System at Boreholes 9, A, 4/7
ITEM | DESCRIPTION | UNIT | QTY | Rate(KES) | Amount(KES)
BOREHOLE 9
5.13.1 | RSI 3 x 380V IP66 22kW 46A | Pc | 1
5.13.2 | Solar Panels 270W poly crystalline | Pc | 96
5.13.3 | DC Disconnect 1000-40-5 | Pc | 2
5.13.4 | Manual Changeover switch 160A | Pc | 1
5.13.5 | Well Probe Sensor | Set | 1
5.13.6 | PV Protect 1000-125 | Pc | 1
5.13.7 | Surge Protector | Pc | 2
5.13.8 | PV Combiner 1000-125-4 | Pc | 1
5.13.9 | 10 mm2 4 core armoured underground cable | m | 50
5.13.10 | 0.75mm2 Well Probe Cable | m | 150
5.13.11 | 1.5mm2 Armoured Underground cable for the Well probe | m | 30
5.13.12 | 10mm2 Twin Flat with Earth for panel interwiring | m | 80
5.13.13 | 10mm2 Earth Cable | m | 20
5.13.14 | Installation Sundry | Unit | 1
5.13.15 | 5m High Ground mount mild steel support structure | Lump sum | 1
5.13.16 | 25mm UPVC Airline | m | 42
5.13.18 | Earth rod c/w clamp | pc | 2
5.13.19 | 10mm2 Copper Earth Cable | m | 10
5.13.20 | Lightning Arrestor | Set | 1
5.13.21 | Non Return Valve (Flap Type) DN75 | pc | 1
5.13.22 | GI Pipes Class B, DN75 , 6m long with crane sockets | pcs | 8
BOREHOLE 7
5.13.26 | PSk2-40 Controller-controller with DataModule, Sunswitch | Pc | 1
5.13.27 | Solar Panels 270W poly crystalline | Pc | 84
5.13.28 | DC Disconnect 1000-40-5 | Pc | 2
5.13.29 | Well Probe Sensor | Set | 1
5.13.30 | PV Protect 1000-125 | Pc | 1
5.13.31 | Surge Protect | Pc | 2
5.13.32 | PV Combiner 1000-125-4 | Pc | 1
5.13.33 | PS Communicator with 7Ah Battery and 20W Solar Panel and 1 year license access | Set | 1
5.13.34 | 10 mm2 4 core armoured underground cable | m | 50
5.13.35 | 0.75mm2 Well Probe Cable | m | 70
5.13.36 | 1.5mm2 Armoured Underground cable for the Well probe | m | 30
5.13.37 | 10mm2 Twin Flat with Earth for panel interwiring | m | 80
5.13.38 | 10mm2 Earth Cable | m | 20
5.13.39 | Installation Sundry | Unit | 1
5.13.40 | 5m High Ground mount mild steel support structure | Lump sum | 1
5.13.41 | 25mm UPVC Airline | m | 42
5.13.42 | Earth rod c/w clamp | pc | 2
5.13.43 | 10mm2 Copper Earth Cable | m | 10
5.13.44 | 60A Manual Change over switch | Pc | 1
5.13.45 | Lightning Arrestor | Set | 1
5.13.46 | Non Return Valve (Flap Type) DN75mm | pc | 1
5.13.47 | GI Pipes Class B, DN75 , 6m long with crane sockets | pcs | 8
Total Page 1
BOREHOLE 4
5.13.50 | PSk2-40 Controller-controller with Data Module, Sunswitch | Pc | 1
5.13.51 | Solar Panels 270W poly crystalline | Pc | 84
5.13.52 | DC Disconnect 1000-40-5 | Pc | 2
5.13.53 | Well Probe Sensor | Set | 1
5.13.54 | PV Protect 1000-125 | Pc | 1
5.13.55 | Surge Protect | Pc | 2
5.13.56 | PV Combiner 1000-125-4 | Pc | 1
5.13.57 | PS Communicator with 7Ah Battery and 20W Solar Panel and 1 year license access | Set | 1
5.13.58 | 10 mm2 4 core armoured underground cable | m | 50
5.13.59 | 0.75mm2 Well Probe Cable | m | 70
5.13.60 | 1.5mm2 Armoured Underground cable for the Well probe | m | 30
5.13.61 | 10mm2 Twin Flat with Earth for panel interwiring | m | 80
5.13.62 | 10mm2 Earth Cable | m | 20
5.13.63 | Installation Sundry | Unit | 1
5.13.64 | 5m High Ground mount mild steel support structure | Lump sum | 1
5.13.65 | 25mm UPVC Airline | m | 42
5.13.66 | Earth rod c/w clamp | pc | 2
5.13.67 | 10mm2 Copper Earth Cable | m | 10
5.13.68 | 60A Manual Change over switch | Pc | 1
5.13.69 | Lightning Arrestor | Set | 1
5.13.70 | Non Return Valve (Flap Type) DN75 | pc | 1
5.13.71 | GI Pipes Class B, DN75 , 6m long with crane sockets | pcs | 8
BOREHOLE A
5.13.73 | RSI 3 x 380V IP66 22kW 46A | Pc | 1
5.13.74 | Solar Panels 270W poly crystalline | Pc | 96
5.13.75 | DC Disconnect 1000-40-5 | Pc | 2
5.13.76 | Manual Changeover switch 160A | Pc | 1
5.13.77 | Well Probe Sensor | Set | 1
5.13.78 | PV Protect 1000-125 | Pc | 1
5.13.79 | Surge Protect | Pc | 2
5.13.80 | PV Combiner 1000-125-4 | Pc | 1
5.13.81 | 10 mm2 4 core armoured underground cable | m | 50
5.13.82 | 0.75mm2 Well Probe Cable | m | 150
5.13.83 | 1.5mm2 Armoured Underground cable for the Well probe | m | 30
5.13.84 | 10mm2 Twin Flat with Earth for panel interwiring | m | 80
5.13.85 | 10mm2 Earth Cable | m | 20
5.13.86 | Installation Sundry | Unit | 1
5.13.87 | 5m High Ground mount mild steel support structure | Lump sum | 1
5.13.88 | 25mm UPVC Airline | m | 42
5.13.89 | Earth rod c/w clamp | pc | 2
5.13.90 | 10mm2 Copper Earth Cable | m | 10
5.13.91 | Lightning Arrestor | Set | 1
5.13.92 | Non Return Valve (Flap Type)DN75 | pc | 1
5.13.93 | GI Pipes Class B, DN75 , 6m long with crane sockets | pcs | 8
Total Page 2
TOTAL CARRIED TO BILLL 5 SUMMARY SHEET

## Bill 5_Summary Sheet
PART 5 - REHABILITATION AND DRILLING OF BOREHOLES
BILL No. | DESCRIPTION | UNIT | QTY | Rate (KES) | Amount (KES)CONFIRMED BILLS | Amount (KES)PROVISIONAL BILLS
BILL 5 SUMMARY SHEET
CONFIRMED BILLS
5.1 | BORE HOLE A
5.2 | BORE HOLE C
5.3 | BORE HOLE D2, D3
5.4 | BORE HOLE E
5.5 | BORE HOLE G1, G2
5.6 | BORE HOLE 1
5.7 | BORE HOLE 2
5.8 | BORE HOLE 4, 7
5.9 | BORE HOLE 6.1. 6.2
5.10 | BORE HOLE 8.1, 8.2,8.3
5.11 | BORE HOLE 9
PROVISIONAL BILLS
5.12 | TIWI BORE HOLE MONITORING SYSTEM
5.13 | BOREHOLE SOLAR PV SYSTEM
BILL No. 5- CARRIED TO GRAND SUMMARY

## 6
PART 6 - Collector Mains: Borehole 4&7 and BH A to Connection on Kaya Bombo Main
ITEM | DESCRIPTION | UNIT | QTY | RATE (KES) | AMOUNT(KES) | Rate(Tshs) | Rate(Tshs) | Amount(Tshs)
6.1 | Demolition and Site Clearance
6.1.1 | General clearance
6.1.1.1 | Agricultural land | ha | 0.65
6.1.2 | Open bush and thicket
6.1.2.1 | locally disposed | ha | 0.4
6.1.3 | Removal of Trees and Stumps
6.1.3.1 | Trees girth 500mm-1m locally disposed | No | 1
6.1.3.2 | Stumps of diameter 500 mm- 1m | No | 1
6.1.3.3 | Stumps of diameter : exc 1m but n.e. 3m locally disposed | No | 1
6.1.4 | CLEARANCE OF PIPELINE WAYLEAVES, DISPOSAL LOCALLY
6.1.4.1 | Nominal bore: upto 300 mm Pipeline only | m | 1663
6.1.5 | REMOVAL OF ANT AND TERMITE HILLS AND NESTS
6.1.5.1 | Along pipeline routes, excess material locally disposed | m3 | 2
6.1.6 | LANDSCAPING
6.1.6.1 | Land scaping,plant trees, replant indigenous plants include for environmental impact mitigation | LS | 1
6.2 | PIPE-FITTINGS- SUPPLY(PN12)
Note: Pipes and fittings requirements, sizes, quantities, etc to be determined in liaison with the Engineer prior to ordering
WATER MAINS
This position includes provision, transporting to site, lowering into trench, laying, alining to line and level, and jointing of pipes.
6.2.1 | HDPE pipes
6.2.1.1 | HDPE pipes DN150 mm, PE100 PIN 12 | m | 1663
6.2.2 | FITTINGS TO HDPE PIPES
6.2.2.1 | Bend 90°, DN150 PN 12, | No. | 1
6.2.3 | JUNCTIONS AND BRANCHES, ALL FLANGED, MIN PN12
6.2.3.1 | Tees branch down 6 diameter, 150/150 mm diameter | No | 2
6.2.3.2 | Tees branch down 7 diameter, 150/150 mm diameter | No | 2
6.2.4 | JUNCTIONS AND BRANCHES, MAIN PLAIN ENDED, BRANCH FLANGED, MIN PN12
6.2.4.1 | Tees branch down, 150/150 | No | 2
6.2.4.2 | Tees branch down, 150/100 | No | 2
6.2.4.3 | Tees branch down, 150/80 | No | 2
6.2.4.4 | Tees branch down, 150/50 | No | 2
TOTAL PAGE 1
6.2.5 | JUNCTIONS AND BRANCHES, MAIN SOCKETED, BRANCH FLANGED FOR AIR VALVES, MIN PN12
6.2.5.1 | Tees branch down 6 diameter, 150/150 mm diameter | No | 5
6.2.5.2 | Main socketed c/w flanged invert level , branch for Washouts, Min PN12, 150/150 mm diameter | No | 2
6.2.5.3 | Tapers, double flanged, Min PN12, Concentric, down as stated, 150/80 mm diameter | No | 5
6.2.5.4 | Plain ended & Single flanged pieces, Min PN12 - 150 mm dia. Length=1000mm | No | 7
6.2.5.5 | Plain ended pipe pieces-length n.e. 1.0 mc/w centre puddle flange, 150 mm dia. Length=1000mm | No | 7
6.2.5.6 | Single flanged pipe pieces, 150 mm dia. Length=1000mm | No | 7
6.2.5.7 | Single flanged pipe pieces ,length n.e. 1.0 m, c/w centre puddle flange - 50 mm dia. Length = 500 mm | No | 7
6.2.5.8 | Single flanged pipe pieces ,length n.e. 1.0 m, c/w centre puddle flange - 80 mm dia. Length = 1000 mm | No | 7
6.2.5.9 | Single flanged pipe pieces ,length n.e. 1.0 m, c/w centre puddle flange - 100 mm dia. Length = 1000 mm | No | 7
6.2.5.10 | Flexible, straignt coupling to suit steel pipes, 150 mm dia | No | 7
6.2.5.11 | Flexible, Wide range/stepped coupling to suit GI/uPVC, 150 mm dia | No | 7
6.2.5.12 | Flexible, Flanged adaptor, to suit steel pipes, 150 mm dia | No | 7
6.2.5.13 | Flexible, Flanged adaptor, to suit steel pipes, 200 m dia | No | 6
6.2.5.14 | Flanged adaptor, flexible to suit GI/uPVC, 80 mm dia | No | 4
6.2.6 | FITTINGS IN UPVC TO SUIT UPVC PIPES
6.2.6.1 | Bends 45⁰, double socked, Min. PN16 - DN 160 mm | No | 2
6.2.7 | VALVES,PENSTOCKS, HYDRANTS, METERS
6.2.7.1 | Gate valves to SSRN 226 c/w T-Keys, Resilient seal series 14 Min PN12 - DN 80 mm | No | 2
6.2.7.2 | Gate valves to SSRN 226 c/w T-Keys, Resilient seal series 14 Min PN12 - DN 100 mm | No | 2
6.2.7.3 | Butterfly section valves with rising spindle c/w T-keys, Min. PN12 - DN 150 mm | No | 2
6.2.7.4 | Flap Valves(Washout) Min PN12 - DN 150 mm | No | 4
6.2.7.5 | Air valves, Non-slam air valve or equivalent with Isolating valve 25 mm double air acting and surge suppressing air valve c/w isolating integral valve PN12 | No | 5
6.2.7.6 | Flanged Float Valves Min PN12 - 150 mm diameter | No | 2
6.2.7.7 | Zonal Bulk Meters, Flanged Woltman Type Min PN12 - DN 150 mm | No | 2
6.2.7.8 | Meter Strainer, double flanged, Min PN12 - DN 150 mm | No | 2
6.2.8 | METHOD OF MEASUREMENT TYPE A IN METERS
HDPE pipes and fittings
6.2.8.1 | Pipe n.b exc 100mm but n.e. 400mm trenches depth 0-1.0m | m | 271
6.2.8.2 | Pipe n.b exc 100mm but n.e. 400mm trenches depth 1-1.5m | m | 1092
6.2.8.3 | Pipe n.b exc 100mm but n.e. 400mm trenches depth 1.5-2m | m | 300
Installation of HDPEwashout pipes
6.2.8.4 | Pipe n.b. exc 100 mm but n.e. 200 mm trenches 1.5-2m | m | 36
TOTAL PAGE 2
PRESSURE TESTING HDPE PIPES AND FITTINGS: Ref Specs. 9.2.6.1
6.2.8.5 | Test pressure exc 12 bars but not exc 16 bars pipe n.b. exc. 100mm but n.e. 400mm | m | 1663
STERILIZATION AND FLUSHING
6.2.8.6 | Pipe n.b100mm-400mm | m | 1663
METHOD OF MEASUREMENT TYPE B BY NUMBER
Bends, Double Flanged
11.25deg, 22.5deg, 45deg, 90deg, Long radious bends
6.2.8.7 | Nb exc.100 but n.e. 400 mm - Not in trenches | No | 2
6.2.8.8 | Nb exc.100 but n.e. 400 mm - In trenches depth 1-1.5 m | No | 9
Bends, Double Socketed
11.25deg, 22.5deg, 45deg, 90deg, Long radious bends
6.2.8.9 | Nb. n.e 100 mm in trenches , depth n.e. 1m | No | 1
6.2.8.10 | Nb. n.e 100 mm in trenches , depth n.e. 1-1.5m | No | 1
Junctions and Branches
All flanged Tees
6.2.8.11 | Nb exc 200 mm but n.e 400 mm in trenches depth 1-1.5 m | No | 1
6.2.8.12 | Nb exc 200 mm but n.e 400 mm in trenches depth 1.5-2 m | No | 1
Tapers
6.2.8.13 | Nb exc 100 mm but n.e. 200 mm in trenches depth n.e. 1m | No | 2
6.2.8.14 | Nb exc 100 mm but n.e. 200 mm in trenches depth 1-1.5m | No | 2
Single flanged pipe pieces, length n.e. 1.0 m
6.2.8.15 | NB. Exc 100mm but n.e. 200 mm in trenches depth n.e.1m | No | 1
6.2.8.16 | NB. Exc 100mm but n.e. 200 mm in trenches depth 1-1.5m | No | 1
Single flanged pipe pieces, length n.e. 1.0 m - c/w centre puddle flange
6.2.8.17 | Nb- ne 100 mm in trenches, depth n.e 1.0 m | No | 1
6.2.8.18 | Nb- ne 100 mm in trenches, depth 1-1.5 m | No | 1
6.2.8.19 | Nb- exc. 100 mm but ne 200 mm in trenches, depth 1-1.5 m | No | 1
Double flanged pipe pieces
6.2.8.20 | Nb.exc 100 mm but ne 400 mm in trenches 1-1.5m | No | 7
6.2.8.21 | Nb.exc 100 mm but ne 400 mm in trenches 1.5-2m | No | 7
Adaptors, detachable Collars Couplings &saddles
Flexible, Flanged adaptor, PN 12 to suit steel pipes
6.2.8.22 | Nb. ne 100 mm in trenches, depth n.e 1m | No | 2
6.2.8.23 | Nb. ne 100 mm in trenches, depth n 1-1.5m | No | 2
6.2.8.24 | Nb- exc. 100 mm but ne 200 mm in trenches, depth ne 1 m | No | 2
Flanged adaptor, flexible to suit GI/uPVC pipes PN12
6.2.8.25 | Nb. Ne 100 mm in trenches, depth ne 1m | No | 2
6.2.8.26 | Nb. Ne 100 mm in trenches, depth ne 1-1.5m | No | 2
TOTAL PAGE 3
6.3 | PIPEWORK
6.3.1 | MANHOLE AND OTHER CHAMBERS IN ACCORDANCE WITH STANDARD DRAWINGS
6.3.1.1 | In-situ concrete outfall structure(washout) pipe nom exc. 100, but not ne 200 depth 1.5-2m | No | 2
6.3.1.2 | Precast Concrete air valve chamber pipe nb exc . 200 mm, but ne 400 mm depth ne 1.5 m | No | 5
6.3.1.3 | Masonry or dense blockwork Bulk Meter chamber pipe - nb not exc 100 mm depth exc1.5m | No | 2
6.3.1.4 | Masonry or dense blockwork strainer chamber pipe - nb not exc 100 mm depth exc1.5m | No | 2
6.3.2 | MANHOLE COVERS
6.3.2.1 | Composite covers 1500 mm dia medium duty, in concrete with key | No | 13
6.3.3 | CROSSINGS
6.3.3.1 | Fence crossing pipe nom. Bore ne 200-400 mm | No | 15
6.3.3.2 | Sewer, ditch or drain crossing pipe nom. Bore ne 200-400 mm(Provisional) | No | 3
6.3.4 | REINSTATEMENT
6.3.4.1 | Breaking up, temporary and permanent reinstatement of tarmac roads, pipe nom.bore100-400 mm | m | 24
6.3.4.2 | Breaking up, temporary and permanent reinstatement of dirt roads, pipe nom.bore100-400 mm | m | 18
6.3.5 | OTHER PIPEWORK ANCILLARIES
6.3.5.1 | Marker Posts for Sluice valves in accordance with std drgs | No | 2
6.3.5.2 | Marker Posts for Air valves in accordance with std drgs | No | 5
6.3.5.3 | Marker Posts for Washout valves in accordance with std drgs | No | 2
6.3.5.4 | Marker Posts for Pipelines in accordance with std drgs | No | 6
6.3.6 | COVERS AND SURFACE BOXES
6.3.6.1 | HDPE valve surface boxes, medium duty with locable cover and frame in (500 x 500 x 200) mm class 20 concrete surround as per standard drawing: area 0.1-0.5 m2 | No | 2
6.3.6.2 | Concrete chamber covers with locable Composite covers and frame 600 mm dia. Medium duty, with key. Area 1-5 m2 | No | 13
6.3.6.3 | Fixed length Extension Spindles c/w protection sleeve to suit gate valves, Length = 800 mm | No | 2
6.4 | PIPEWORK SUPPORTS & PROTECTION ANCILLARIES TO LAYING & EXCAVATION
6.4.1 | EXTRAS TO EXCAVATION AND BACKFILLING
6.4.1.1 | In pipe trenches excavation or rock class I material (Provisional) | m3 | 223
6.4.1.2 | In pipe trenches excavation or rock class II material (Provisional) | m3 | 230
6.4.1.3 | In pipe trenches backfilling with class S2 material (Provisional) | m3 | 2370
6.4.1.4 | In manhole and chambers excavation of rock class II material (Provisional) | m3 | 2
6.4.2 | BEDS
6.4.2.1 | Selected granular materiall with blended imported and screened class S2 material pipe 200-400 mm (Provisional) | m3 | 177
6.4.3 | SURROUNDINGS
6.4.3.1 | Selected granular material incl upper bedding, side filling and initial backfill with blended imported and screened class S2 material pipe 200-400 mm (Provisional) | m3 | 237
6.4.4 | CONCRETE STOOLS AND THRUST BLOCKS CONCRETE CLASS 20
To Horizontal bends
6.4.4.1 | Volume 0.5-1 m3, nom bore 200-400 mm | No | 12
TOTAL PAGE 4
To Vertical bends at Crest
6.4.4.2 | Volume 0.1-0.2 m3 nom bore 100-200 mm(Provisional) | No | 1
6.4.4.3 | Volume 0.5-1 m3 nom bore 100-200 mm(Provisional) | No | 1
To Junctions
6.4.4.4 | Volume 0.5-1m3, bore 200-400 mm | No | 2
To Tapers
6.4.4.5 | Volume 0.1-0.2 m3, nom bore 200-400 mm | No | 6
To Valves
6.4.4.6 | Volume n.e. 0.1 m3 for valve n.b. not exc 100 mm | No | 13
TOTAL PAGE 5
TOTAL CARRIED TO GRAND SUMMARY

## 6A_Marereheadworks
PART 6A: MARERE HEADWORKS IMPROVEMENT- EXPANSION OF FLOW DIVISION/CHLORINATION CHAMBER (as per Tech Spec chapter 16 and drawing N° 1220/K/002A))
ITEM | DESCRIPTION | UNIT | QTY | RATE (KES) | AMOUNT(KES)
6A.1 | Demolition and Site Clearance |  |  |  | 0
6A.1.1 | Demolition of existing masonry weir/scour chamber (approx. dimensions 1200x1200mm) | Item | 1
6A.1.2 | Disconnection of connected pipework (2x DN160 uPVC discharge pipes, DN50 steel scour pipe and gate valve) | Item | 1
6A.1.3 | Removal of demolition material, cleaning and preparation of ground for new structure | Item | 1
6A.1.4 | Demolition of the existing RC side wall of the existing chlorine dosing chamber (approximate length= 2000mm) | Item | 1
6A.3 | Concrete construction & masonry work
6A.3.1 | Volume n.e. 50-100 m3 | Item | 1
6A.3.2 | Expand RC chlorine dosing chamber by 500 mm lengthwise to make it a proportional flow division chamber for the flows into the existing DN500 and the new DN250 pipes; Ensure water tightness according to specifications for water retaining structures | Item | 1
6A.3.3 | New cover to fit to expanded RC chlorine dosing chamber and to allow manual adjustment of both gate valves comfortably | Item | 1
6A.3.4 | Reconstruction of the entire weir/sour chamber (1200 x 1200 mm, masonry) | Item | 1
6A.4 | PIPE- FITTINGS- SUPPLY-(PN10)
6A.4.1 | Extension of existing 2x DN 160 uPVC drainage pipes to reconstructed and replaced weir/scour chamber. Supply, connect to existing pipes | Item | 1
6A.4.2 | DN50 steel scour pipe and gate valve - supply and installation between new chlorine dosing chamber and new weir/scour chamber | Item | 1
Valves, Penstocks, Hydrants, Meters
6A.4.3 | Gate Valves to SSRN 226 c/w T-keys, Resilient seal series 14 - 250 mm diameter plus 2 T-Keys | No | 1
6A.4.3 | Gate Valves to SSRN 226 c/w T-keys, Resilient seal series 14 - 500 mm diameter plus 2 T-Keys | No | 1
Bill 6a: TOTAL CARRIED TO GRAND SUMMARY

## 7
PART 7 - Transmission Pipeline (Marere Pipeline)
ITEM | DESCRIPTION | UNIT | QTY | RATE(KES) | AMOUNT(KES) | Rate(Tshs) | Rate(Tshs) | Amount(Tshs)
7.1 | Demolition and Site Clearance
7.1.1 | General clearance
7.1.1.1 | Agricultural land | ha | 4
7.1.2 | Open bush and thicket
7.1.2.1 | locally disposed | ha | 4
7.1.3 | Dense bush and thicket
7.1.3.1 | locally disposed | ha | 4
7.1.4 | Forest
7.1.4.1 | locally disposed | ha | 4
7.1.5 | Removal of Trees and Stumps
7.1.5.1 | Trees girth 500mm-1m - locally disposed | No | 1
7.1.5.2 | Trees girth 1-2m - locally disposed | No | 2
7.1.5.3 | Stumps of diameter 500 mm- 1m | No | 3
7.1.5.4 | Stumps of diameter : exc 1m but n.e. 3m locally disposed | No | 1
7.1.6 | CLEARANCE OF PIPELINE WAYLEAVES, DISPOSAL LOCALLY
7.1.6.1 | Nominal bore: upto 300 mm, Pipeline only: | m | 6368
7.1.7 | REMOVAL OF ANT AND TERMITE HILLS AND NESTS
7.1.7.1 | Along pipeline routes, excess material locally disposed- | m3 | 100
7.1.8 | LANDSCAPING
7.1.8.1 | Land scaping,plant trees, replant indigenous plants include for environmental impact mitigation | m3 | 10
7.2 | PIPE-FITTINGS- SUPPLY(HDPE PIN25)
Note: Pipes and fittings requirements, sizes, quantities, etc to be determined in liaison with the Engineer prior to ordering
WATER MAINS
7.2.1 | HDPE pipes
7.2.1.1 | (a) Pipes HDPE-PE100 , PN25 - 250 mm | m | 2844
| (b) Pipes HDPE-PE100, PN25 - 200 mm | m | 3524
7.2.1.2 | Double flanged pipe pieces, L=0.5 m - 250 mm | No | 1
7.2.1.3 | Double flanged pipe pieces, L=1.0 m - 200 mm | No | 1
7.2.1.4 | Double flanged pipe c/w puddle flange pieces, L=1.0 m - 250 mm | No | 1
7.2.1.5 | Washout Outfall Pipes, Supply of UPVC Pipes, PVC-U S&S to SSRN 300- Min PN10 - 160 mm diameter | m | 200
TOTAL PAGE 1
7.2.3 | JUNCTIONS AND BRANCHES, ALL FLANGED, MIN PN25
7.2.3.1 | Tees branch - 250/200 mm diameter | No | 1
7.2.3.2 | Tees branch - 200/200 mm diameter | No | 1
7.2.4 | JUNCTIONS AND BRANCHES, MAIN PLAIN ENDED, BRANCH FLANGED, MIN PN25
7.2.4.1 | Tees branch - 250/150 | No | 2
7.2.4.2 | Tees branch - 250/100 | No | 2
7.2.4.3 | Tees branch - 200/80 | No | 2
7.2.4.4 | Tees branch - 200/50 | No | 2
7.2.5 | JUNCTIONS AND BRANCHES, MAIN SOCKETED, BRANCH FLANGED FOR AIR VALVES, MIN PN25
7.2.5.1 | Tees branch - 250/150 mm diameter | No | 5
7.2.5.1 | Tees branch - 200/150 mm diameter | No | 6
7.2.6 | a) Main socketed c/w flanged invert level , branch for Washouts, Min PN25 - 250/150 mm diameter | No | 5
| b) Main socketed c/w flanged invert level , branch for Washouts, Min PN25 - 200/150 mm diameter | No. | 6
7.2.7 | a) Tapers, double flanged, Min PN25, Concentric, down as stated - 250/80 mm diameter | No | 5
| b) Tapers, double flanged, Min PN25, Concentric, down as stated - 200/80 mm diameter | No | 6
7.2.8 | Plain ended & Single flanged pieces, Nominal lengths as stated, Min PN25
7.2.8.1 | Plain ended pieces - 250 mm dia. Length=1000mm | No | 2
7.2.8.2 | Plain ended pipe pieces-length n.e. 1.0 mc/w centre puddle flange - 250 mm dia. Length=1000mm | No | 1
7.2.8.3 | Single flanged pipe pieces - 150 mm dia. Length=1000mm | No | 3
7.2.8.4 | Single flanged pipe pieces ,length n.e. 1.0 m, c/w centre puddle flange - 50 mm dia. Length = 500 mm | No | 12
7.2.8.5 | Single flanged pipe pieces ,length n.e. 1.0 m, c/w centre puddle flange - 80 mm dia. Length = 1000 mm | No | 3
7.2.8.6 | Single flanged pipe pieces ,length n.e. 1.0 m, c/w centre puddle flange - 100 mm dia. Length = 1000 mm | No | 3
7.2.8.7 | Single flanged pipe pieces ,length n.e. 1.0 m, c/w centre puddle flange - 150 mm dia. Length = 1000 mm | No | 14
7.2.8.8 | Single flanged pipe pieces ,length n.e. 1.0 m, c/w centre puddle flange - 200 mm dia. Length = 1000 mm | No | 6
7.2.9 | Adaptors, detachable, Collars couplings & saddles, Min PN25
7.2.9.1 | Flexible, straight coupling to suit steel pipes - 250 mm dia | No | 2
7.2.9.2 | Flexible, straight coupling to suit steel pipes - 200 mm dia | No | 2
7.2.9.3 | Flexible, Wide range/stepped coupling to suit GI/UPVC - 150 mm dia | No | 8
7.2.9.4 | Flexible, Flanged adaptor, to suit steel pipe - 50 mm dia | No | 12
7.2.9.5 | Flexible, Flanged adaptor, to suit steel pipe - 80 mm dia | No | 3
7.2.9.6 | Flexible, Flanged adaptor, to suit steel pipe - 100 mm dia | No | 3
7.2.9.7 | Flexible, Flanged adaptor, to suit steel pipe - 150 mm dia | No | 14
7.2.9.8 | Flexible, Flanged adaptor, to suit steel pipe - 200 m dia | No | 6
7.2.9.9 | Flanged adaptor, flexible to suit GI/uPVC - 50 mm dia | No | 3
7.2.9.10 | Flanged adaptor, flexible to suit GI/uPVC - 80 mm dia | No | 3
7.2.9.11 | Flanged adaptor, flexible to suit GI/uPVC - 100 mm dia | No | 2
7.2.9.12 | Flanged adaptor, flexible to suit GI/uPVC - 150 mm dia | No | 12
7.2.9.13 | Flanged adaptor, flexible to suit GI/uPVC - 200 m dia | No | 3
TOTAL PAGE 2
7.2.10 | FITTINGS IN UPVC TO SUIT UPVC PIPES
7.2.10.1 | Bend, double socked, Min. PN16 - 45⁰ DN 160 mm | No | 10
7.2.11 | VALVES, PENSTOCKS, HYDRANTS, METERS
7.2.11.1 | Gate valve to SSRN 226 c/w T-Keys, Resilient seal series 14 Min PN25 - DN 50 mm | No | 1
7.2.11.2 | Gate valve to SSRN 226 c/w T-Keys, Resilient seal series 14 Min PN25 - 80 mm dia | No | 1
7.2.11.3 | Gate valve to SSRN 226 c/w T-Keys, Resilient seal series 14 Min PN25 - 100 mm dia | No | 2
7.2.11.4 | Gate valve to SSRN 226 c/w T-Keys, Resilient seal series 14 Min PN25 - 150 mm dia | No | 21
7.2.11.5 | Gate valve to SSRN 226 c/w T-Keys, Resilient seal series 14 Min PN25 - 200 m dia | No | 21
7.2.11.6 | Butterfly section valves with rising spindle c/w T-keys, Min. PN25 - DN 250 mm | No | 5
7.2.11.7 | Butterfly section valves with rising spindle c/w T-keys, Min. PN25 - DN 200 mm | No | 6
7.2.11.8 | Flap Valves(Washout) Min PN25 - 150 mm diameter | No | 11
7.2.11.9 | Air valves, Non-slam air valve or equivalent with Isolating valve - 25mm double air acting and surge suppressing air valve, c/w isolating integral valve PN25 | No | 12
7.2.11.10 | Master Meter(Electromagnetic), According to specifications, MinPN25 - 200 mm dia | No | 2
7.2.11.11 | Master Strainer, double flanged, Min PN25 - 250 mm dia | No | 2
7.2.11.12 | Master Strainer, double flanged, Min PN25 - 200 mm dia | No | 1
7.3 | PIPEWORK
PIPES, SEWERS &FITTINGS-INSTALL
7.3.1 | METHOD OF MEASUREMENT TYPE A IN METERS
7.3.1.1 | HDPE pipes - Pipe n.b exc 200mm but n.e. 400mm trenches depth 1-1.5m | m | 53
7.3.1.2 | HDPE pipes - Pipe n.b exc 200mm but n.e. 400mm trenches depth 1-1.5m | m | 340
7.3.1.3 | HDPE pipes - Pipe n.b exc 200mm but n.e. 400mm trenches depth 1.5-2m | m | 1200
7.3.1.4 | HDPE pipes - Pipe n.b exc 200mm but n.e. 400mm trenches depth 2-3m | m | 3822
7.3.1.5 | HDPE pipes - Pipe n.b exc 200mm but n.e. 400mm trenches depth 3-4m | m | 628
7.3.1.6 | HDPE pipes - Pipe n.b exc 200mm but n.e. 400mm trenches depth 4-6m | m | 200
7.3.1.7 | HDPE pipes - Pipe n.b exc 200mm but n.e. 400mm on concrete piers varied height(0.5-2m) | m | 132
Replacement of Existing Air Valves at Mwache River Creek
7.3.1.8 | Removal of existing air valve and replacing with Non-slam air valve or equivalent with Isolating valve - 25 mm double air acting and surge suppressing air valve, c/w isolating integral valve PN25 | No. | 2
Installation of Flow Control Valve at Kaya Bombo Junction
7.3.1.9 | Allow for removal of existing DN500 gate valve and replacing with DN500 Flow Control Valve PIN25 including all excavations, Chamber chamber modifications,supply and installation of fittings as instructed by the Engineer and as shown on Drg 1220/K/010/A | No. | 1
Installation of uPVC washout pipes
7.3.1.10 | Pipe n.b. exc 100 mm but n.e. 200 mm trenches 1.5-2m | m | 200
PRESSURE TESTING HDPE PIPES; Ref. Specs 9.2.6.1
7.3.1.11 | Test pressure exc 25 bars but not exc 40 bars - pipe n.b. exc. 200mm but n.e. 400mm | m | 6368
STERILIZATION AND FLUSHING
7.3.1.12 | Pipe n.b 200mm-400mm | m | 6368
TOTAL PAGE 3
7.3.2 | METHOD OF MEASUREMENT TYPE B BY NUMBER
Bends, Double Flanged
11.25deg, 22.5deg, 45deg, 90deg, Long radious bends
7.3.2.1 | Nb exc.200 but n.e. 400 mm - Not in trenches | No | 1
7.3.2.2 | Nb exc.200 but n.e. 400 mm - In trenches depth 1-1.5 m | No | 1
Bends, Double Socketed
11.25deg, 22.5deg, 45deg, 90deg, Long radious bends
7.3.2.3 | Nb. N.e 100 mm in trenches , depth n.e. 1m | No | 2
7.3.2.4 | Nb. N.e 100 mm in trenches , depth n.e. 1-1.5m | No | 3
11.25deg, 22.5deg, 45deg, 90deg, Long radious bends
7.3.2.5 | Nb. Exc 100 but n.e. 200 mm in trenches 1-1.5 m | No | 8
7.3.2.6 | Nb. Exc 100 but n.e. 200 mm in trenches 1.5-2 m | No | 19
11.25deg, 22.5deg, 45deg, 90deg, Long radious bends
7.3.2.7 | Nb. Exc 200 mm but n.e 400 mm in trenches 1-1.5m | No | 16
7.3.2.8 | Nb. Exc 200 mm but n.e 400 mm in trenches 1.5-2m | No | 19
Junctions and Branches
7.3.2.9 | All flanged Tees - Nb exc 200 mm but n.e 400 mm in trenches depth 1-1.5 m | No | 1
7.3.2.10 | All flanged Tees - Nb exc 200 mm but n.e 400 mm in trenches depth 1.5-2 m | No | 2
7.3.2.11 | Main Plan ended, Branch flanged in trenche - Nb exc 200 mm but n.e 400 mm in trenches depth 1-1.5 m | No | 2
7.3.2.12 | Main Plan ended, Branch flanged in trenche - Nb exc 200 mm but n.e 400 mm in trenches depth 1.5-2 m | No | 3
7.3.2.13 | Main socketed, Branch flanged - Nb exc 200 mm but n.e 400 mm in trenches depth 1-1.5 m | No | 11
7.3.2.14 | Main socketed, Branch flanged - Nb exc 200 mm but n.e 400 mm in trenches depth 1.5-2 m | No | 10
7.3.2.15 | Main Socketed, Branch flanged, invert level - Nb exc 200 mm but n.e 400 mm in trenches depth 1-1.5 m | No | 11
7.3.2.16 | Main Socketed, Branch flanged, invert level - Nb exc 200 mm but n.e 400 mm in trenches depth 1.5-2 m | No | 10
Tapers
7.3.2.17 | Nb exc 100 mm but n.e. 200 mm in trenches depth n.e. 1m | No | 11
7.3.2.18 | Nb exc 100 mm but n.e. 200 mm in trenches depth 1-1.5m | No | 10
Pipe pieces and bellmouths
7.3.2.19 | Plain ended pieces, Nb.exc 200 mm but ne 400 mm in trenches 1-1.5m | No | 1
7.3.2.20 | Plain ended pieces, Nb.exc 200 mm but ne 400 mm in trenches 1.5-2m | No | 1
7.3.2.21 | Plain ended pieces, length n.e. 1m c/w centre puddle flange - Nb.exc 200 mm but ne 400 mm in trenches 1-1.5m | No | 1
7.3.2.22 | Single flanged pipe pieces, length n.e. 1.0 m - NB. Exc 100mm but n.e. 200 mm in trenches depth n.e.1m | No | 2
7.3.2.23 | Single flanged pipe pieces, length n.e. 1.0 m - NB. Exc 100mm but n.e. 200 mm in trenches depth 1-1.5m | No | 2
7.3.2.24 | Single flanged pipe pieces, c/w centre puddle flange - Nb- ne 100 mm in trenches, depth n.e 1.0 m | No | 3
7.3.2.25 | Single flanged pipe pieces, c/w centre puddle flange - Nb- ne 100 mm in trenches, depth 1-1.5 m | No | 11
7.3.2.26 | Single flanged pipe pieces, c/w centre puddle flange - Nb- exc. 100 mm but ne 200 mm in trenches, depth 1-1.5 m | No | 7
7.3.2.27 | Double flanged pipe pieces - Nb.exc 200 mm but ne 400 mm in trenches 1-1.5m | No | 1
7.3.2.28 | Double flanged pipe pieces - Nb.exc 200 mm but ne 400 mm in trenches 1.5-2m | No | 2
TOTAL PAGE 4
Adaptors, detachable Collars Couplings &saddles
7.3.2.29 | Flexible, strainght coupling to suit ferrous pipe - Nb.exc 200 mm but ne 400 mm in trenches 1-1.5m | No | 6
7.3.2.30 | Flexible, strainght coupling to suit ferrous pipe - Nb.exc 200 mm but ne 400 mm in trenches 1.5-2m | No | 5
7.3.2.31 | Flexible, wide range/stepped coupling - Nb- exc. 100 mm but ne 200 mm in trenches, depth ne 1m | No | 7
7.3.2.32 | Flexible, wide range/stepped coupling - Nb- exc. 100 mm but ne 200 mm in trenches, depth 1-1.5m | No | 7
7.3.2.33 | Flexible, Flanged adaptor, PN 16 to suit steel pipes - Nb. ne 100 mm in trenches, depth n.e 1m | No | 6
7.3.2.34 | Flexible, Flanged adaptor, PN 16 to suit steel pipes - Nb. ne 100 mm in trenches, depth n 1-1.5m | No | 4
7.3.2.35 | Flexible, Flanged adaptor, PN 16 to suit steel pipes - Nb- exc. 100 mm but ne 200 mm in trenches, depth ne 1 m | No | 6
7.3.2.36 | Flexible, Flanged adaptor, PN 16 to suit steel pipes - Nb- exc. 100 mm but ne 200 mm in trenches, depth 1-1.5 m | No | 6
7.3.2.37 | Flexible, Flanged adaptor, PN 16 to suit steel pipes - Nb.exc 200 mm but ne 400 mm in trenches 1-1.5m | No | 5
7.3.2.38 | Flexible, Flanged adaptor, PN 16 to suit steel pipes - Nb.exc 200 mm but ne 400 mm in trenches 1.5-2m | No | 3
7.3.2.39 | Flanged adaptor, flexible to suit GI/uPVC pipes PN16 - Nb. Ne 100 mm in trenches, depth ne 1m | No | 6
7.3.2.40 | Flanged adaptor, flexible to suit GI/uPVC pipes PN16 - Nb. Ne 100 mm in trenches, depth ne 1-1.5m | No | 5
7.3.2.41 | Flanged adaptor, flexible to suit GI/uPVC pipes PN16 - Nb- exc. 100 mm but ne 200 mm in trenches, depth 1-1.5 m | No | 6
TOTAL PAGE 5
7.4 | PIPEWORK
7.4.1 | MANHOLE AND OTHER CHAMBERS IN ACORDANCE WITH STANDARD DRAWINGS
7.4.1.1 | In-situ concrete outfall structure(washout) pipe nom exc. 100 but not ne 200 depth 1.5-2m | No | 11
7.4.1.2 | Precast Concrete air valve chamber pipe nb exc . 200 mm but ne 400 mm depth ne 1.5 m | No | 12
7.4.1.3 | Masonry or dense blockwork Bulk Meter chamber pipe nb not exc 100 mm depth exc1.5m | No | 2
7.4.1.4 | Masonry or dense blockwork Master Meter chamber pipe nb not exc 100 mm depth exc1.5m | No | 2
7.4.1.5 | Masonry or dense blockwork strainer chamber pipe - nb not exc 100 mm depth exc1.5m | No | 3
7.4.2 | MANHOLE COVERS
7.4.2.1 | Composite covers 1500 mm dia medium duty, in concrete with key | No | 43
7.4.2.2 | Precast concrete: Area 1-2 m2(rate only) | No | 43
7.4.3 | CROSSINGS
7.4.3.1 | River, stream or canal, Pemba river crossing with 80-90m, pipe nom DN 200-500 mm, undercrossing pipe with a width equal to DN + 500 mm from each side, the pipe should be burried to a depth of 1000mm + DN (150 mm stone packing in mortar, 50 mm Mortar base, 250 mm reinforced concrete class C25/30 for ceiling, bottom slab, as per general drawing. the work shall include the excavation, bedding, concrete and backfilling | No | 1
7.4.3.2 | Fence crossing - pipe nom. Bore ne 200-400 mm(Provisional) | No | 1
7.4.3.3 | Sewer, ditch or drain crossing - pipe nom. Bore ne 200-400 mm (Provisional) | No | 5
7.4.4 | REINSTATEMENT
7.4.4.1 | Breaking up, temporary and permanent reinstatement of tarmac roads, pipe nom.bore200-400 mm (Provisional) | m | 3
7.4.4.2 | Breaking up, temporary and permanent reinstatement of dirt roads, pipe nom.bore200-400 mm (Provisional) | m | 1
7.4.5 | OTHER PIPEWORK ANCILLARIES
7.4.5.1 | Marker Posts for Sluice valves in accordance with std drgs | No | 24
7.4.5.2 | Marker Posts for Air valves in accordance with std drgs | No | 11
7.4.5.3 | Marker Posts for Washout valves in accordance with std drgs | No | 10
7.4.5.4 | Marker Posts for Pipelines in accordance with std drgs | No | 31
7.5 | COVERS AND SURFACE BOXES
7.5.1 | HDPE valve surface boxes, medium duty with locable cover and frame in (500 x 500 x 200) mm class 20 concrete surround as per standard drawing: area 0.1-0.5 m2 | No | 10
7.5.2 | Concrete chamber covers with locable Composite covers and frame 600 mm dia. Medium duty, with key. Area 1-5 m2 | No | 46
7.5.3 | Fixed length Extension Spindles c/w protection sleeve to suit gate valves, Length = 800 mm | No | 24
TOTAL PAGE 6
7.6 | PIPEWORK SUPPORTS & PROTECTION ANCILLARIES TO LAYING & EXCAVATION
7.6.1 | EXTRAS TO EXCAVATION AND BACKFILLING
7.6.1.1 | In pipe trenches excavation or rock class I material | m3 | 728
7.6.1.2 | In pipe trenches excavation or rock class II material | m3 | 1395
7.6.1.3 | In pipe trenches backfilling with class S2 material | m3 | 6000
7.6.1.4 | In manhole and chambers excavation of rock class II material | m3 | 930
7.6.2 | BEDS
7.6.2.1 | Selected granular materiall with blended imported and screened class S2 material pipe 200-400 mm | m3 | 11440
7.6.3 | SURROUND
7.6.3.1 | Selected granular material incl upper bedding, side filling and initial backfill with blended imported and screened class S2 material pipe 200-400 mm | m3 | 850
7.6.4 | CONCRETE STOOLS AND THRUST BLOCKS CONCRETE
CLASS 20
To Horizontal bends
7.6.4.1 | Volume 0.5-1 m3, nom bore 200-400 mm | No | 20
To Vertical bends at Crest
7.6.4.2 | Volume 0.1-0.2 m3 nom bore 100-200 mm | No | 6
7.6.4.3 | Volume 0.5-1 m3 nom bore 100-200 mm | No | 3
To Vertical bends at Trough
7.6.4.4 | Volume 0.1-0.2 m3, nom bore 100-200 mm | No | 5
7.6.4.5 | Volume 0.5-1 m3, nom bore 100-200 mm | No | 5
To Junctions
7.6.4.6 | Volume 0.5-1m3, bore 200-400 mm | No | 30
To Tapers
7.6.4.7 | Volume 0.1-0.2 m3, nom bore 200-400 mm | No | 43
To Valves
7.6.4.58 | Volume n.e. 0.1 m3 for valve n.b. not exc 100 mm | No | 43
7.7 | MISCELLANEOUS
7.7.1 | T-keys for valve operation
7.7.1.1 | Provide T-keys for the operatiob of Sluice Valves. Length=800 mm c/w tapered handle tip for surface box opening. Keys to suit extended spindle top provided | No | 5
TOTAL PAGE 7
TOTAL CARRIED TO GRAND SUMMARY -

## 8
PART 8 - Chlorine Dosing Unit at Kaya Bombo and Magodzoni (quantities are for 2 units)
ITEM | DESCRIPTION | UNIT | QTY | RATE(KES) | AMOUNT(KES)
8.1 | DEMOLITION AND SITE CLEARANCE
8.1.1 | SITE CLEARANCE
8.1.1.1 | Excavation of topsoil depth n.e. 250 mm | m³ | 5.16
8.1.2 | EXCAVATIONS
8.1.2.1 | Excavation in normal material (maximum depth 0.25 to 0.5 m) | m³ | 12.5
8.1.2.2 | Excavation in normal material (maximum depth 0.5 to 1 m) | m³ | 12.5
8.1.2.3 | Excavation in normal material (maximum depth 1m to 2 m) | m³ | 25
8.1.2.4 | Item for excavation in rock (depth not exceeding 0.25 m) | m³ | 0.49
8.1.2.5 | Item for excavation in rock (maximum depth 0.25 to 0.5m ) | m³ | 0.49
8.1.2.6 | Item for excavation in rock (maximum depth 0.5 to 1 m) | m³ | 0.98
8.1.2.7 | Item for excavation in rock (maximum depth 1 to 2 m) | m³ | 0.67
8.1.2.8 | Trimming of excavated surfaces in top soil | m² | 25
8.1.2.9 | Trimming of excavated surfaces in rock | m² | 1
8.1.2.10 | Preparation of excavated surface in rock, material other than topsoil, rock or artificial hard material | m² | 25
8.1.2.11 | Preparation of excavated surafce in rock | m² | 1
8.1.2.12 | Disposal of surplus excavated materials other than topsoil, rock or artificial hard material/ to designated site within free haul distance of 5.0 km | m² | 5
8.1.2.13 | Ditto but rock | m³ | 1
8.1.2.14 | Filling to structures: selected excavated materials other than rock or top soil | m³ | 10
8.1.2.15 | Imported rock compacted on site | m³ | 1
8.2 | Concrete work
8.2.1 | Provision of Concrete, designed mix for ordinary structural concrete
8.2.1.1 | Class 15 | m³ | 1.25
8.2.1.2 | Class 25/20 | m³ | 21.5
8.2.2 | Placing
8.2.2.1 | Mass Blinding thickness not exceeding 50 mm | m³ | 1.25
8.2.3 | Place Reinforced Concrete
8.2.3.1 | Bases, footings, pile caps and ground slabs thickness between 150 mm to 300 mm thick | m³ | 1.6
8.2.3.2 | Reinforced concrete in beams (cross section) 0.1 - 0.26 m² | m³ | 3.52
8.2.3.3 | Reinforced concrete in slabs | m³ | 16.5
8.3 | Formwork
8.3.1 | Rough formwork to edges of floor slab 0.2 - 0.40 m | m² | 25
Fair Faced Fomwork
8.3.2 | Plane, bertical; 0.2 - 0.4 m wide | m² | 50.4
8.4 | Reinforcement
Steel Reinforced - High yield steel bars to BS 4449
8.4.1 | Y-8 | t | 0.5
8.4.2 | Y-16 | t | 1.48
8.4.3 | Fabrick mesh reinforcement, | m² | 20.64
TOTAL PAGE 1
8.5 | Walling, Dense concrete block, solid block to BS 2028 type A
8.5.1 | 150 mm thick vertical straight walls | m² | 10.88
8.5.2 | 230mm thick vertical straight walls | m² | 66.6
8.5.3 | Ancillaries
8.5.3.1 | 200 mm wide damp proof course | m | 19.8
8.5.4 | Miscellaneous
8.5.4.1 | Hardcore fill | m³ | 7.5
8.5.4.2 | 250µm damp proof membrane | m² | 20.64
8.5.5 | Suspended ceilings
8.5.5.1 | Depth of suspension not exceeding 150 mm | m² | 25
8.5.6 | Carpentry and joinery
8.5.6.1 | Structural and carcassing timber; Trussed rafters and roof trusses span 14.8 m; double tie beam and rafters 50 mm x 150 mm; struts 100 x 50 and purlins 75 x 50 | No | 3
8.5.6.2 | Supply and installation of metal walkway connecting Chemical Dosing Unit to the reservoir as shown on the drawings | LS | 2
8.6 | Finishes
8.6.1 | Floors; Porcelain chemical resistant non slippery tiles laid on a 40 mm cement sand mortar bedding ratio 1:3 cement to sand | m² | 25.5
8.6.2 | Walls, internal cement sand plaster thickness 12 mm of cement sand ratio 1:3 | m² | 88.36
8.6.3 | Walls, external cement sand plaster thickness 20 mm of cement sand of ratio 1:3 | m² | 66.6
8.6.4 | Allow for fabrication, supply and installation of handrail as shown on drawings | No | 2
8.6.5 | 3 coats of Weatherguard paint to smooth plastered blockwork external upper surfaces inclined at an angle not exceeding 30 degrees to the horizontal | m² | 66.6
8.6.6 | 3 coats of Weatherguard paint to smooth plastered blockwork internal upper surfaces inclined at an angle not exceeding 30 degrees to the horizontal | m² | 88.36
8.6.7 | Profiled IT5 sheet in one layer upper surface inclined at an angle not exceeding 30 degrees to the horizontal | m² | 40.35
8.6.8 | 3 coats of Oil paint to Timber surfaces width not exceeding 300 | m | 20.68
8.6.9 | Plastic gutters 100 mm | m | 19.6
8.6.10 | Fitting to gutters | No | 4
8.6.11 | Downpipes 100 mm | m | 7.4
8.6.12 | Fittings to downpipes; 90 degrees bends | No | 4
8.7 | Mixing Tanks and Dosers
8.7.1 | Construction of Chemical Mixing Tanks including electric stirrers, installing and commissioning including all pipeworks, fittings and valves and 6mm thick disolving tray | LS | 2
8.7.2 | Supply all materials construction of concrete pipe ducts as per drawings and installation of PE chemical pipes as specified including excavations and making good. | LS | 2
8.7.3 | Supply and installation of electric agitators as specified on drawings | No | 2
TOTAL PAGE 2
8.7.4 | Gravity solution feeder, constant level tank with inlet connector, repentor, outer funnel and 50 mm tubing for outlet. Includes valves and chemical resistant tubing. Flow upto 15-20 ml/s | No | 2
8.8 | Walkway
8.8.1 | Provide all materials and construct walkway to connect the dosing structure to the tank as shown on drawings. Length of walkway is 2.0 m. Include for installation of handrails along the walkway. | LS | 1
8.9 | PIPEWORK-PIPES, AND FITTINGS- SUPPLY
8.9.1 | uPVC pipes to SSRN 301, Class PN6, with socket and spigot joints to SSRN 0
8.9.1.1 | Nominal bore: 90 mm, nominal length- 6000 mm | No | 24
8.9.1.2 | Nominal bore: 25mm, nominal length 6000 mm | No | 12
8.9.2 | UPVC pipe fittings to SSRN 302, Junctions and branches, main flanged
8.9.2.1 | Tee, equal, branch as main nb 90 mm | No | 2
8.9.2.2 | Tee, equal, branch as main, nb 25 mm | No | 2
8.9.3 | Bends, double socket, to SSRN 0
8.9.3.1 | Short radius, 90 degrees, nb 90 mm | No | 2
8.9.3.2 | Short radius, 90 degrees, nb, 25 mm | No | 2
8.9.4 | Standard Couplers and end pieces
8.9.4.1 | Threaded- p.e.coupler 90 mm x 3" | No | 8
8.9.5 | Valves, penstocks, hydrants, meters
8.9.5.1 | Flanged, non-rising spindle with handwheel nb, 80 mm | No | 4
8.9.6 | Valves
8.9.6.1 | Tap threaded 25 mm | No | 8
8.10 | PIPEWORK- PIPES AND FITTINGS - INSTALL
8.10.1 | METHOD OF MEASUREMENT TYPE B
UPVC pipes and fittings
8.10.1.1 | Pipes not in trenches, nom bore not exc 110 mm | No | 40
8.10.1.2 | Bends not in trenches, nom.bore: not exc. 110 mm | No | 4
8.10.1.3 | Junctions: Not in trenches, nom. Bore not exc 110 mm | No | 4
8.10.1.4 | Couplers: Not in trenches, nom. Bore not exc. 100 mm | No | 8
8.10.1.5 | Valves: Not in trenches, nom bore not exc 110 mm | No | 12
TOTAL PAGE 3
TOTAL CARRIED TO GRAND SUMMARY -

## 9.Small works
PART 9 - Provisional Bill : Small Works
ITEM | DESCRIPTION | UNIT | QTY | RATE(KES) | AMOUNT(KES)
9.1 | Rehabilitation of 1140 m³ Kaya Bombo reservoir
Ref. Drawing No..1210/008A-009A
9.1.1 | Removal of Sediments and Cleaning
9.1.1.1 | Cleaning of reservoir with high pressure water jet and/or high pressure air | LS | 1
9.1.1.2 | Identification and repair of major concrete defects and cracks | LS | 1
9.1.2 | OTHER
9.1.2.1 | Supply all materials and rehabilitate reservoir wall and ensure water tightness in accordance with specifications. Include for cleaning the internal wall faces, surface preparation and application of waterproof plastering(with silica agent) over the entire wall face(approx. 540 m2). Include for cleaning external wall, surface preparation and repaint the entire outer wall face of the tank(approximately 520 m2). Include for repair for bottom slab, sections of spalled concrete by applying epoxy mortar or other equally approved materials. Include for construction of (50x100 mm) edge beam around the bottom slab approximately 50 m as per drawing. | LS | 1
9.1.2.2 | Remove existing sealant, clean and prepare 20mm groove around the tank perimeter and apply polysulphide sealand with a gun as per detail on drawing and ensure reservoir is water tight in accordance with Specifications. | m | 50
9.2 | Construction of VIP Latrines- 9Nos
Locations to be indicated by the Engineer
VIP Latrines - Masonry building will be constructed in accordance with drawing No.1230/K/017A
9.2.1 | Excavate in normal soil below ground level, include for timbering, dewatering during construction of the foundation for the walls, to the dimension and levels as shown on the drawings, backfilling and compacting after completion of the works upto the required levels and cart away the surplus materials to be used on site or elsewhere or dumped away as directed, complete as specified and shown on the drawings. | m3 | 160
9.2.2 | Extra over 1.01 for excavation in Class I material(Rock) | m3 | 22
9.2.3 | Ditto but for Class III Material | m3 | 16
9.2.4 | Provide, lay and compact hardcore as Special below the kiosk floor or in other places as directed to the dimensions and levels as shown on the drawings. | m3 | 8
9.2.5 | Provide, mix, place and compact concrete(1:4:8 mix) as blinding layer 50 mm think under the bottom of pit as shown on the drawing | m2 | 160
9.2.6 | Provide, mix, place and compact class 20 in the foundations, floor and lintel(reinforced), include for formwork shuttering , reinforcement and all required materials and workmanship complete as specified on the drawings. | m3 | 35
TOTAL PAGE 1
9.2.7 | Provide and build dressed masonry walls with quarry stone using 1:3 cement sand mortarfor the laterines walls and pit to the required dimensions and shapes as specified on the drawings. | m2 | 320
9.2.8 | Provide all materials and install doors to the required dimensions as detailed on the drawings, inclde for door frame, hinges, locks and keys, materials and workmanship to make it complete. | No | 10
9.2.9 | Provide all materials and install windows as specified. Include for frames, hinges, screws,and workmanship to make it complete. | No | 10
9.2.10 | Provide all materials and construct roof to the VIP latrine as specified on drawings | No | 10
9.2.11 | Provide all materials and apply one undercoat and 3 finishing coats to the walls, doors and windows both externally and internally of the VIP latrines | m2 | 600
9.2.12 | Provide all all materials and lay non-slip floor tiles as specified. | m2 | 40
9.3 | FENCING AND GATE- 10 Nos Sites
9.3.1 | Excavate for post holes, provide all materials and construct chain link fence on concrete posts at 3m centres all as per details on Drg. No. 1230/k/015A-016A, including straining posts at every 10th post and additional posts at corners | m | 3200
9.3.2 | Provide all materials and construct metal gate 3600mm widex 2000mm high with 1 Nr. 915mm wide pedestrian gate including 3 Nr. Pillars all as detailed on Drg. No. 1230/K/015A-016A | No | 10
TOTAL PAGE 2
TOTAL CARRIED TO GRAND SUMMARY - Provisional Sum

## 10.Dayworks
PART 10 - Provisional Sums -Confirmed: SCHEDULE OF DAYWORK RATES AND SPECIFIED QUANTITIES FOR DAYWORK
ITEM | BRIEF DESCRIPTION | UNIT | QTY | RATE(KES) | AMOUNT(KES)
Dayworks are subject to the Conditions of Contract and the Specifications of the Contract.
NOTE: THE WHOLE OF THIS BILL IS PROVISIONAL.
THE QUANTITIES INDICATED ARE THE MINIMUM AND DO NOT INCLUDE TRAVEL AND INSTALLATION TIMES FOR EQUIPMENT AND MACHINERY
10.1 | Labour
The rates inserted herein shall include for all costs such as insurance, travelling time, overtime, accommodation, use and maintenance of small tools of trade, supervision, overheads and profit. Only time engaged upon work shall be paid for.
10.1.1 | Unskilled labourer | Hr | 1200
10.1.2 | Electrician | Hr | 400
10.1.3 | Stone mason | Hr | 400
10.1.4 | Carpenter | Hr | 400
10.1.5 | Concretor | Hr | 400
10.1.6 | Certified welder | Hr | 400
10.1.7 | Pipelayer | Hr | 400
10.1.8 | Painter | Hr | 400
10.1.9 | Engineering surveyor | Hr | 400
10.1.10 | Foreman | Hr | 400
10.1.11 | Watchman (including use of firewood, lights, day, night, Sunday and Public Holiday watching) | Hr | 2000
10.1.12 | Qualified engineering supervisor | Hr | 1600
10.1.13 | Qualified water supply technician (min. 15 years experience) | Hr | 1200
10.2 | Plant and Equipment
The rates inserted herein shall include for all operational and maintenance costs, fuel, oil, grease, operators, turnboys, supervision, overhead and profits. Only the time actually employed on works shall be paid for and the rates shall include for idle time.
10.2.1 | Compressor complete (3.0 m³/minute) | Hr | 600
10.2.2 | Mobile generator 15kVA | Hr | 1200
10.2.3 | Concrete vibrator (petrol or diesel) | Hr | 600
10.2.4 | Concrete mixer 14/10 (including batch weighing gear and drag feed shovel) | Hr | 600
10.2.5 | Dumper 0.38 m³ | Hr | 600
10.2.6 | Compactor / roller, dead weight 9 tonnes | Hr | 100
10.2.7 | Lorry (tipper) 5 tonne | Hr | 400
10.2.8 | Lorry (tipper) 7 tonne | Hr | 200
10.2.9 | Portable water pump 50 mm diameter (inclusive of hoses, couplings, etc.) | Hr | 600
10.2.10 | Oxy-acetylene cutting and welding set, including oxygen and acetylene | Hr | 300
10.2.11 | Electric welding set including electrodes | Hr | 300
10.2.12 | 4-WD pickup 1 tonne | Hr | 1600
10.2.13 | Jack hammer 25 kg | Hr | 200
10.2.14 | Mobile crane 5 tonnes | Hr | 800
10.2.15 | Air compressor (5,000 l/min) | Hr | 400
10.2.16 | Pressure testing equipment (including diesel engine for pump) | Hr | 400
10.2.17 | Acoustic ground microphones for leak detection | Hr | 480
10.3 | Materials
All materials shall comply with the Specifications. The rates inserted herein shall include for delivery to site, storage, handling, overheads and profits. The quantities indicated herein are only the minimum.
10.3.1 | Quick drying hydraulic mortar for leak repairs | Kg | 300
10.3.2 | Ordinary portland cement | Kg | 600
10.3.3 | Mild steel (any size from 8mm to 25mm dia.) | Kg | 200
TOTAL PAGE 1
10.3.4 | High tensile steel (any size from 8mm to 15mm dia.) | Kg | 200
10.3.5 | Reinforcement fabric mesh size A142 weighing 2.22 kg/m2. | m2 | 100
10.3.6 | Building sand | m³ | 100
10.3.7 | Coarse aggregate for concrete | m³ | 200
10.3.8 | Use of shuttering timber | m2 | 100
10.3.9 | Imported murram fill | m³ | 100
10.3.10 | Concrete block 200 mm thick | No | 100
10.3.11 | Concrete block 150 mm thick | No | 200
10.3.12 | Hard core | m³ | 500
10.3.13 | Concrete ogee pipe, DN 300 mm | m | 500
10.3.14 | Concrete Class 15/20 | m³ | 200
10.3.15 | Concrete Class 20/20 | m³ | 200
10.3.16 | Concrete Class 25/20 | m³ | 200
10.3.17 | Lubricants | L | 50
10.3.18 | Chlorinated paint | L | 50
10.3.19 | Emulsion paint | L | 50
10.3.20 | Gloss paint | L | 50
10.3.21 | Super petrol | L | 3000
10.3.22 | Diesel | L | 2000
10.3.23 | HDPE pipe, PN 10 bars, DN 40 mm | m | 2000
10.3.24 | HDPE pipe, PN 10 bars, DN 25 mm | m | 4000
10.3.25 | HDPE pipe, PN 10 bars, DN 20 mm | m | 6000
10.3.26 | Steel compression coupling, PN 10 bars, Straight DN 40 mm | No | 200
10.3.27 | Steel compression coupling, PN 11 bars, Straight DN 150 mm | No | 400
10.3.28 | Steel compression coupling, PN 12 bars, Straight DN 100 mm | No | 600
10.3.29 | Steel compression coupling, PN 12, Reducer DN 150-100 mm | No | 200
10.3.30 | Steel compression coupling, PN 12, Reducer DN 150 / 75 mm | No | 400
10.3.31 | Steel compression coupling, PN 12, Reducer DN150 / 50mm | No | 600
10.4 | Transportation
Hourly rates including km-lump-sums
10.4.1 | Vehicles | Hr | 80
10.4.2 | Trucks | Hr | 80
TOTAL PAGE 2
TOTAL CARRIED TO Grand Summary - Dayworks

## Grand Summary
GRAND SUMMARY
Contract Name: | EMERGENCY WORKS FOR INCREASING WATER AVAILABILITY IN LIKONI
NCB No. | Contract No. CWSB/AFD/W1/2019
| DESCRIPTION | PAGE | AMOUNT | AMOUNT
|  |  | (KES): CONFIRMED SCOPE AMOUNTS | (KES): PROVISIONAL BILLS ONLY
CONFIRMED BILLS
Bill No. 1 | Preliminary and General Items
Bill No. 2 | Combined Hydraulic- Chemical Borehole Rehabilitation
Bill No. 4 | Drilling,Construction, Testing Pumping of 2No. Boreholes ( 1Nr at A nd and 1nr at 9)
Bill No. 5 | Rehabilitation and Equiping of Boreholes and Installation of Monitoring System(Bills 5.1-5.11)
Bill No. 6 | Collection Mains: BH 4, 7 and BH A to Connection on Kaya Bombo Main
Bill No. 6A | Marere Headworks Improvements- Expansion of Flow Division/Chlorination Chamber
Bill No. 7 | Marere Parallel Pipeline Construction
Bill No. 8 | Chlorine Dosing Unit at Kaya Bombo and Magodzoni
Bill No.10 | Schedule of Dayworks
| Sub-Total Bill No.1, 2,4, 5.1-5.11, 6, 6A, 7, 8 and 10: | A
| Add Provisional Sum for Contingency Allowance( =10% *A ) | B
| Sub-Total 1(A+B) | C
| Allow for all Local Taxes and Duties including 16% VAT on sub-total (C) | D
| SUB-TOTAL CONFIRMED BILLS(C+D) | E
PROVISIONAL BILLS
Bill No. 3 | Geophysical Investigations
Bill No. 5.12 | Tiwi Borehole Monitoring System
Bill No. 5.13 | Solar PV at Borehole A, 4/7 and 9
Bill No.9 | Small Works (Rehabilitation of 1140 m3 reservoir, VIP Latrines, Fencing and Gates)
| Sub-Total Bill No. 3. 5.12. 5.13 and 9 : To Provisional Bill Column | F
| Add Provisional Sum for Contingency Allowance( =10% *F ) | G
| Sub-Total 1(F+G) | H
| Allow for all Local Taxes and Duties including 16% VAT on sub-total (H) | I
| SUB-TOTAL PROVISIONAL BILLS(H+I) | J
Bid Price (E + J) (Carried forward to Letter of Bid)
Bidder's Name:
Bidder's Signature:
Date:

## Unit prices
PART 5.14 - Electro-Mechanical Works & Pipeworks Borehole (Site-Repairs)
UNIT PRICES
ITEM | ITEM DESCRIPTION | UNIT | Quantity | Rate(KES) | Delivery To Site(KES) | Amount(KES)
A | Bareshaft Borehole Submersible pump c/w 4 core tail cable;
A1 | Capacity 9 m3/hr, 130 metres head | Nr | 1
A2 | Capacity 9 m3/hr, 150 metres head | Nr | 1
A3 | Capacity 9 m3/hr, 165 metres head | Nr | 1
A4 | Capacity 9 m3/hr, 180 metres head | Nr | 1
A5 | Capacity 12 m3/hr, 125 metres head | Nr | 1
A6 | Capacity 12 m3/hr, 140 metres head | Nr | 1
A7 | Capacity 12 m3/hr, 165 metres head | Nr | 1
A8 | Capacity 12 m3/hr, 180 metres head | Nr | 1
A9 | Capacity 15 m3/hr, 135 metres head | Nr | 1
A10 | Capacity 15 m3/hr, 150 metres head | Nr | 1
A11 | Capacity 15 m3/hr, 165 metres head | Nr | 1
A12 | Capacity 15 m3/hr, 185 metres head | Nr | 1
A13 | Capacity 22 m3/hr, 120 metres head | Nr | 1
A14 | Capacity 22 m3/hr, 135 metres head | Nr | 1
A15 | Capacity 22 m3/hr, 150 metres head | Nr | 1
A16 | Capacity 22 m3/hr, 165 metres head | Nr | 1
A17 | Capacity 22 m3/hr, 175 metres head | Nr | 1
A18 | Capacity 22 m3/hr, 190 metres head | Nr | 1
A19 | Capacity 30 m3/hr, 130 metres head | Nr | 1
A20 | Capacity 30 m3/hr, 140 metres head | Nr | 1
A21 | Capacity 30 m3/hr, 155 metres head | Nr | 1
A22 | Capacity 40 m3/hr, 125 metres head | Nr | 1
A23 | Capacity 40 m3/hr, 135 metres head | Nr | 1
A24 | Capacity 40 m3/hr, 150 metres head | Nr | 1
A25 | Capacity 40 m3/hr, 170 metres head | Nr | 1
A26 | Capacity 46 m3/hr, 120 metres head | Nr | 1
A27 | Capacity 46 m3/hr, 130 metres head | Nr | 1
A28 | Capacity 46 m3/hr, 150 metres head | Nr | 1
A29 | Capacity 46 m3/hr, 180 metres head | Nr | 1
A30 | Capacity 50 m3/hr, 185 metres head | Nr | 1
A31 | Capacity 50 m3/hr, 130 metres head | Nr | 1
A32 | Capacity 50 m3/hr, 140 metres head | Nr | 1
A33 | Capacity 50 m3/hr, 150 metres head | Nr | 1
A34 | Capacity 50 m3/hr, 165 metres head | Nr | 1
B | Bareshaft 3 phase Borehole Submersible Motor c/w 4 core cu, tail cable;
B1 | Rating 7.5 Kw | Nr | 1
B2 | Rating 9.2 Kw | Nr | 1
B3 | Rating 11 Kw | Nr | 1
B4 | Rating 15 Kw | Nr | 1
B5 | Rating 18.5 Kw | Nr | 1
B6 | Rating 22 Kw | Nr | 1
B7 | Rating 26 Kw | Nr | 1
B8 | Rating 30 Kw | Nr | 1
B9 | Rating 37.2 Kw | Nr | 1
B10 | Rating 45 Kw | Nr | 1

## Unit prices 2
UNIT PRICES
ITEM | ITEM DESCRIPTION | UNIT | Quantity | Rate Excluding VAT(KES) | Delivery To Site(KES) | Amount(KES)
C | 6 Metres Length Galvanised water Pipes
C1 | Heavy Class Threaded PIN12
C1.1 | DN50 | Nr | 1
C1.2 | DN65 | Nr | 1
C1.3 | DN100 | Nr | 1
C1.4 | DN150 | Nr | 1
C1.5 | DN200 | Nr | 1
C2 | Heavy Class Flanged-PIN12
C2.1 | DN50 | Nr | 1
C2.2 | DN65 | Nr | 1
C2.3 | DN100 | Nr | 1
C2.4 | DN150 | Nr | 1
C2.5 | DN200 | Nr | 1
D | 3 PHASE ELECTRIC MOTOR STARTER PANELS
D1 | SOFT START- STARTER PANELS
D1.1 | 7.5 Kw | Nr | 1
D1.2 | 9.2 Kw | Nr | 1
D1.3 | 11 Kw | Nr | 1
D1.4 | 15 Kw | Nr | 1
D1.5 | 18.5 Kw | Nr | 1
D1.6 | 22 Kw | Nr | 1
D1.7 | 26 Kw | Nr | 1
D1.8 | 30 Kw | Nr | 1
D1.9 | 37.2 Kw | Nr | 1
D1.10 | 45 Kw
D2 | DIRECT-ON LINE STARTER PANELS
D2.1 | 5.5 Kw | Nr | 1
D2.2 | 7.5 Kw | Nr | 1
D2.3 | 9.2 Kw | Nr | 1
E | CABLES
E1 | PVC SWA PVC COPPER CABLES
E1.1 | 1.5 mm2/2 core | Rolls | 1
E1.2 | 2.5 mm2/2 core | Rolls | 1
E1.3 | 4 mm2/4 core | Rolls | 1
E1.4 | 6 mm2/4 core | Rolls | 1
E1.5 | 10 mm2/4 core | Rolls | 1
E1.6 | 16 mm2/4 core | Rolls | 1
E1.7 | 25 mm2/4 core | Rolls | 1
E1.8 | 35 mm2/4 core | Rolls | 1
E1.9 | 50 mm2/4 core | Rolls | 1
E2 | DOUBLE INSULATED RUBBER WATER TIGHT SUBMERSIBLE COPPER CABLES
E2.1 | 0.75 mm2 single core | Rolls | 1
E2.2 | 1.5 mm2/2 core | Rolls | 1
E2.3 | 4 mm2/4 core | Rolls | 1
E2.4 | 6 mm2/4 core | Rolls | 1
E2.5 | 10 mm2/4 core | Rolls | 1
E2.6 | 16 mm2/4 core | Rolls | 1
E2.7 | 25 mm2/4 core | Rolls | 1
E2.8 | 35 mm2/4 core | Rolls | 1